2013 Integrated Resource Plan Generation Technology Data Book

Prepared for:

Integrated Resource Planning

Prepared by:

Southern Company Generation – Technical Services

December 2012

## INTRODUCTION

The Integrated Resource Plan (IRP) Generation Technology Data Book is published annually by Southern Company Generation staff to provide input for evaluating viable generation technologies for inclusion in plans for meeting future electric power generation needs.

It is important to note that the information provided in the Generation Technology Data Book is intended for planning purposes only and represents average cost and performance data for a "generic" site.  Recipients of this book should be aware that site specific conditions will vary cost and performance data.  Although certain capital cost estimates (e.g. combined cycle) may be more accurate than the others (e.g. nuclear and integrated gasification combined cycle), they should all be considered screening level because they are used concurrently for evaluating future generation technologies.

The following technologies are included in the 2013 IRP Generation Technology Data Book:

Base Load:

- Pulverized Coal (PC) – 850 MW Nominal Supercritical Unit (Illinois #6, PRB)

- Nuclear Advanced Light Water Reactor – 2,234 MW Nominal (2-AP1000 Units)

- Oxygen Blown Integrated Gasification Combined Cycle (IGCC-O) – 600 MW Nominal GE 7FB (2×1 Reference Plant)

- Air Blown IGCC (IGCC-A) – 600 MW Nominal PSDF TRIG GE 7FB (2×1 Reference Plant)

Base / Intermediate Load:

- G-Class (M501G1+ and M501GAC) Natural Gas Only 2×1 Combined Cycle – 850 MW  and 930 MW Nominal

- G-Class (M501G1+ and M501GAC) Dual Fuel 2×1 Combined Cycle – 850 MW and 930 MW Nominal

- F-Class (Siemens SGT6-5000F4) Natural Gas Only 2×1 Combined Cycle (CC) – 750 MW Nominal

- F-Class (Siemens SGT6-5000F4) Dual Fuel 2×1 Combined Cycle (CC) – 750 MW Nominal

Peaking Load:

- F-Class Dual Fuel SGT6-5000F4 Simple Cycle – 350 and 700 MW Nominal

- F-Class Natural Gas Fired SGT6-5000F4 Simple Cycle – 350 and 700 MW Nominal

Renewable Technologies:

- Peak Load Incremental Hydro

- Base Load Landfill Gas to Energy

- Grid-Connected Solar Photovoltaics (PV) – Utility Scale

- Wind Power Generation - Utility Scale

- Biomass Fired– 50 MW Nominal

Appendix:

- Carbon Capture White Paper

- CCS Performance and Cost Adders

- Pumped Storage Hydro

- Compressed Air Energy Storage

- Circulating Fluidized Bed Boiler Power Plant (CFB) – 600 MW Nominal (Lignite based)

- Future Combined Cycle Technology White Paper

- Ultra-Super Critical PC White Paper

Typical information provided for each generation technology is as follows:

- General Description of the Plant

- State of Technology

- Heat Rate and Output including Performance Degradation

- Capital Cost

- Fixed and Variable O&M Cost

- Capital Expenditures for Maintenance

- Emissions Estimates

- Plant Life

- Maintenance Time

- Equivalent Unplanned Outage Rate (EUOR)

- Project Schedule

- Cash Flow Table

Changes in this year's data book include:

- All simple cycle and combined cycle estimates were escalated, and major equipment pricing (CT, HRSG, ST) has been updated wherever possible.

- O&M data updated for all technologies.

  - In particular, the Combined Cycle and Simple Cycle technologies have been revised to better reflect current operational profiles.

- PC technology restricted to Central Appalachian (CAPP) based fuel was removed as an option.  However, the Illinois basin based PC technology is capable of utilizing CAPP as a fuel.  The power, heat rate, cost etc. will be different when using CAPP fuel.

- All indicative project schedules, except Nuclear, have had the project permitting time standardized to 30 months.  This time is considered an average permitting time assuming minimal delays or regulatory issues.  Certain technologies or changes in the regulatory environment could either extend or shorten this time frame.

- Project expenditure data has been revised for each technology to more accurately reflect the project schedule.  The intent of the project expenditure data is to generically show when major outlays will happen (such as major equipment and construction costs), not to reflect all costs that may be necessary for a particular project.  Therefore, periods of very low expenditure relative to the overall plant cost (such as early permitting activities) may be shown as little or no expenditure.

Project Schedules and Cash Flow:

It should be noted that while generic indicative project schedules are provided, actual project schedules could vary based on the unique requirements of the project.  Cash expenditure spread is expressed in percentages instead of the dollar amount to allow for differences between the expenditure spread and the schedule.   The intent of the project expenditure data is to generically show when major outlays will happen (such as major equipment and construction costs), not to reflect all costs that may be necessary for a particular project or the exact time that they will occur.  Due to differentials such as pre-project activities, permitting activities, and post-project invoice spending, the project schedule and expenditure schedule may not be identical.

O&M Scope:

The O&M models were developed by the CC/CT Fleet Strategy organization.  O&M costs are categorized between fixed, variable, and capital expenditure costs.  The scope of each cost is listed below.  All O&M models are assumed to be self-perform models for the life of the plant.

- FIXED:  Fixed O&M costs include plant personnel salaries and benefits, payroll taxes, property insurance, home office and management support but do not include the ad valorem taxes.

- VARIABLE: Variable O&M costs include expenses for consumables, steam turbine maintenance, balance of plant maintenance, and all gas turbine repair parts from scheduled major maintenance.

- CAPITAL EXPENDITURES FOR MAINTENANCE: Capital expenditures for maintenance (CEM) include all new equipment parts or components from scheduled major maintenance and working capital.

EUOR:

EUOR is defined as equivalent unplanned outage factor (forced and maintenance outages and deratings), except for peaking units where EFORd is "demand EFOR" or the probability that the unit will not produce power when demanded.

Capital Cost Scope:

Project costs are grouped in one of the following four categories:

- Engineering, Procurement, and Construction Cost (EPC)

- Site Cost

- Owner’s Cost

- Excluded Cost

Note: All costs are expressed in 1/1/2012 overnight costs and assume an immediate commercial operation date.

EPC:

The EPC cost is equivalent in scope to what a turnkey contractor would quote for the project.  The EPC costs include the following:

- All process equipment and materials associated with the plant (electrical scope to the high side of Generator Step-up Transformer GSU, other terminal points for piping, etc. at the plant boundary line)

- Construction and construction management of all plant equipment and material (includes plant underground work and piling, all temporary construction related equipment, facilities and services)

- Plant engineering, project management and support services

- Gas metering and conditioning station for gas-fired technologies

- On-site rail spur for coal-fired technologies

- EPC cost contingency

Site Cost:

Site related costs include the following components:

- Site preparation costs including site clearing and earthwork (excavation and backfill)

- Site improvements including site drainage, retention ponds, fencing, etc.

- Coal pile and ash/gypsum disposal area preparation

- One mile paved plant access road and paved plant parking lot

- Water source intake and pumping station

- Gas lateral or railroad beyond the plant boundary

- Assumed land cost (“Greenfield” site; plant proper, only)

- Costs associated with collector bus, breakers, and the connection line to the substation which are beyond the high side of the GSU (see sketch on the following page for scope).

Owner’s Cost:

Owner’s costs include the following components:

- Start-up labor and materials

- Pre Commercial Operation Date (COD) capital items such as plant vehicles, forklifts, carts, etc.

- Plant materials and supplies such as furniture, lab equipment and supplies, shop equipment, tools, test instruments, office equipment and supplies, etc.

- Pre COD plant utilities and waste disposal

- Plant spare parts

- Project development costs including permitting, legal, public relations, taxes, insurance, etc.

- Electricity used during construction

- Pre COD fuel cost or revenue from electricity sales

- Taxes

Excluded Cost:

The following costs are not included in the Technology Data Book costs:

- Transmission system upgrades

- Initial fuel inventory

- Emission allowances or offsets

- Non project specific general allocated overheads

- Allowance for Funds Used During Construction (AFUDC)

Generic Generation Site

Typical Connection Configuration

Generation  site

To Substation A

To Substation B

New substation (Typically 230 or 500kV)

Collector bus, breakers, and connecting line(s)

Costs estimates were included for the items encompassed in the circle above and they are (1) required generating site facilities: the collector bus and breakers and (2) transmission connecting line(s) which would be paid for by a generator in accordance with current industry practice.

## ACKNOWLEDGMENTS

Appreciation is extended to the following individuals for their contributions in developing the information presented in this document:

Joe Eiland

John Jones

Dean Sheffield

Kristi Woods

Juan La Rota

Kapil Desai

Zach Fairweather

Leeth DePriest

Tim Pinkston

Zach Looney

Chao Y. Wu

Brian Barham

Mike Smith

Chris Curow

Valeake Smith

Ned West

Nick Irvin

Richard Esposito

Elizabeth Philpot

Krishnan Kandasamy

Kevin Gammill

Kip Jenkins

Albert Hicks

Anthony Scott

Jeff Grubb

Greg Mann

Steve Graham

Chris Habig

Karen Huffman

Ben Carmichael

## Table of contents

DATA SUMMARY (New and Clean)	9

DATA SUMMARY (Degraded)	12

BASE LOAD PULVERIZED COAL	15

BASE LOAD NUCLEAR	34

BASE LOAD INTEGRATED GASIFICATION COMBINED CYCLE OXYGEN BLOWN	43

BASE LOAD INTEGRATED GASIFICATION COMBINED CYCLE AIR BLOWN	56

BASE / INTERMEDIATE LOAD NATURAL GAS ONLY COMBINED CYCLE “G” & “H” TECHNOLOGY	71

BASE / INTERMEDIATE LOAD DUAL FUEL COMBINED CYCLE “G” & “H” TECHNOLOGY	91

BASE / INTERMEDIATE LOAD NATURAL GAS ONLY COMBINED CYCLE “F” TECHNOLOGY	109

BASE / INTERMEDIATE LOAD DUAL FUEL COMBINED CYCLE “F” TECHNOLOGY	122

PEAKING NATURAL GAS SIMPLE CYCLE COMBUSTION TURBINE “F” TECHNOLOGY	134

PEAKING DUAL-FUEL SIMPLE CYCLE COMBUSTION TURBINE “F” TECHNOLOGY	147

RENEWABLE TECHNOLOGIES	161

PEAK LOAD INCREMENTAL HYDRO	162

BASE LOAD LANDFILL GAS TO ENERGY NOMINAL 3.2 MW	167

GRID-CONNECTED SOLAR PHOTOVOLTAICS (PV) – UTILITY SCALE	177

WIND POWER GENERATION - UTILITY SCALE	183

BASE LOAD BIOMASS FIRED	189

APPENDIX	202

CARBON CAPTURE WHITE PAPER, 2012	203

PULVERIZED COAL TECHNOLOGY DISCUSSION	228

CCS PERFORMANCE AND COST ADDERS	233

PUMPED STORAGE HYDRO	234

COMPRESSED AIR ENERGY STORAGE	235

BASE LOAD CIRCULATING FLUIDIZED BED BOILER POWER PLANT	243

FUTURE COMBINED CYCLE TECHNOLOGY WHITE PAPER	255

DATA SUMMARY (New and Clean)—Base / Intermediate Load

DATA SUMMARY (New and Clean)—Peak Load

DATA SUMMARY (Degraded)—Base / Intermediate Load

DATA SUMMARY (Degraded)—Peak Load

# BASE LOAD PULVERIZED COAL

NOMINAL 850 MW

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The unit is based on an 850 MW supercritical once-through sliding pressure, single reheat pulverized coal boiler providing steam at 4000 psi, 1100 F main steam and 1100 F reheat steam to a steam turbine driving a 3600 rpm turbine generator.  Plant cost basis and features include:

- Pulverized coal fired, single re-heat boiler with SCR system

- Tandem-compound, four-flow condensing steam turbine generator

- Dry flue gas desulfurization (DFGD), fabric filter system, and Wet flue gas desulfurization (WFGD) system (Illinois Basin and Central Appalachian fuels only)

- Wet flue gas desulfurization (WFGD) system and fabric filter system (Powder River Basin {PRB} fuel only)

- Material handling systems for fuel, limestone, gypsum and ash and all associated appurtenances

- Eight (8) stages of regenerative feedwater heating will be utilized in a heater above reheat point (HARP) cycle.

- Surface condenser

- Mechanical draft cooling tower

The Facility will include the common shared-support infrastructure for 2 x 850 MW

net electric generating units. The support infrastructure will include:

Railroad facilities

Coal and limestone unloading facilities

Coal reclaim system

Limestone storage and reclaim system

Limestone preparation system

Lime storage system

Gypsum dewatering system

Gypsum stockout and storage system

Single shell stack sized with two flues

Fly ash conveying and storage system

Bottom ash conveying and storage system

Demineralized water system

Condensate storage and transfer system

Closed cooling system

Fire protection system

Instrument compressed air system

Plant drains and wastewater treatment system

Potable water system

Sanitary waste system

Plant DCS

Performance and cost data is provided for units designed to burn Illinois Basin or Powder River Basin coal.

#### State of Technology

###### This is a mature technology and currently available.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

Pulverized Coal – PRB based performance

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Condition | REDACTED | REDACTED |
| Annual Average | REDACTED | REDACTED |
| 75% | REDACTED | REDACTED |
| 50% | REDACTED | REDACTED |
| 30% | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

Performance is net to the high side of the GSU and includes station service.

#### New and Clean Conditions:

Pulverized Coal – Illinois Basin #6 based performance

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Condition | REDACTED | REDACTED |
| Annual Average | REDACTED | REDACTED |
| 75% | REDACTED | REDACTED |
| 50% | REDACTED | REDACTED |
| 30% | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

Performance is net to the high side of the GSU and includes station service.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

#### Degraded Conditions:

Pulverized Coal – PRB based performance

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Condition | REDACTED | REDACTED |
| Annual Average | REDACTED | REDACTED |
| 75% | REDACTED | REDACTED |
| 50% | REDACTED | REDACTED |
| 30% | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

Performance is net to the high side of the GSU and includes station service.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

#### Degraded Conditions:

Pulverized Coal – Illinois Basin #6 based performance

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Condition | REDACTED | REDACTED |
| Annual Average | REDACTED | REDACTED |
| 75% | REDACTED | REDACTED |
| 50% | REDACTED | REDACTED |
| 30% | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

Performance is net to the high side of the GSU and includes station service.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

### TOTAL PLANT COSTS

Pulverized Coal – PRB

#### Nominal 850 MW Site:

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (Two 850 MW Units)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Site Cost includes a land cost of $REDACTED for a two unit site and $REDACTED for a single unit.

Pulverized Coal – Illinois Basin

#### Nominal 850 MW Site:

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (Two 850 MW Units)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Site Cost includes a land cost of $REDACTED for a two unit site and $REDACTED for a single unit.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

Pulverized Coal – PRB (Degraded)

#### Nominal 850 MW Site:

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (Two 850 MW Units)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Site Cost includes a land cost of $REDACTED for a two unit site and $REDACTED for a single unit.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Pulverized Coal – Illinois Basin (Degraded)

#### Nominal 850 MW Site:

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (Two 850 MW Units)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Site Cost includes a land cost of $REDACTED for a two unit site and $REDACTED for a single unit.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

### O & M COSTS

##### Nominal 850 Mw site: Pulverized Coal – PRB

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 1700 MW site: Pulverized Coal – PRB

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 850 Mw site: Pulverized Coal – Illinois Basin#6

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 1700 MW site: Pulverized Coal – Illinois Basin#6

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

##### Nominal 850 Mw site: Pulverized Coal – PRB (Degraded)

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 1700 MW site: Pulverized Coal – PRB (degraded)

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

##### Nominal 850 Mw site: Pulverized Coal – Illinois Basin#6 (degraded)

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 1700 MW site: Pulverized Coal – Illinois Basin#6 (Degraded)

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Illinois basin based PC technology is capable of utilizing Central App fuel.  However, this will result in a different set of performance, cost, and O&M data.

### EMISSIONS

Pulverized Coal

|  | PRB Lbs/MMBtu | Illinois Basin Lbs/MMBtu |
| --- | --- | --- |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) | REDACTED | REDACTED |
| Particulate Matter (PM) | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED |
| Volatile Organics (VOC) | REDACTED | REDACTED |
| Mercury (Hg) | REDACTED | REDACTED |

#### Basis for Emissions Data:

Based on summer ambient conditions (95°F dry bulb, 45% relative humidity, 88°F cooling water), New and Clean performance.

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

Ammonia slip of 2 ppm or less.

For particulate matter, condensables in the wet section of the test train shall not be included as particulates.  In the future, it is likely that condensables will be included in PM emission limitations.

Opacity - 5% (As measured after the fabric filter installation).

PRB Coal.

Illinois Basin #6 – Coal with 2.53% Sulfur.

95% SO2 removal by wet limestone scrubber with forced oxidation.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE – EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat Rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | PRB REDACTED for 850 MW site REDACTED for 1700 MW site Illinois Basin #6 REDACTED for 850 MW site REDACTED for 1700 MW site |

## TECHNOLOGY FORECAST

#### PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present | 2020+ |
| --- | --- | --- |
| Representative Technology: | Pulverized Coal Supercritical Wet Limestone Scrubber SCR | Pulverized Coal Ultra-Supercritical Wet Limestone Scrubber SCR (if business case justifies) |
| Average Annual Heat Rate (New & Clean) | REDACTED | *REDACTED |

* Based upon main steam pressure of 4500 psi and main steam/reheat temperature of 1300/1320 0F.

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

|  | 1-Unit |  |
| --- | --- | --- |
|  | 2013 IRP Expenditure Curve | 2013 IRP Expenditure Curve (Cumulative) |
| Month |  |  |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |
| 63 | REDACTED | REDACTED |
| 64 | REDACTED | REDACTED |
| 65 | REDACTED | REDACTED |
| 66 | REDACTED | REDACTED |
| 67 | REDACTED | REDACTED |
| 68 | REDACTED | REDACTED |
| 69 | REDACTED | REDACTED |
| 70 | REDACTED | REDACTED |
| 71 | REDACTED | REDACTED |
| 72 | REDACTED | REDACTED |
| 73 | REDACTED | REDACTED |
| 74 | REDACTED | REDACTED |
| 75 | REDACTED | REDACTED |
| 76 | REDACTED | REDACTED |
| 77 | REDACTED | REDACTED |
| 78 | REDACTED | REDACTED |
| 79 | REDACTED | REDACTED |
| 80 | REDACTED | REDACTED |
| 81 | REDACTED | REDACTED |
| 82 | REDACTED | REDACTED |
| 83 | REDACTED | REDACTED |
| 84 | REDACTED | REDACTED |
| 85 | REDACTED | REDACTED |
| 86 | REDACTED | REDACTED |

| Pulverized Coal 2-Unit Spending Curve |  |  |  |
| --- | --- | --- | --- |
| Year | Unit 1 | Unit 2 | Total |
| 1 | REDACTED | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED | REDACTED |
| Total | 100% | 100% | 100% |

## indicative PROJECT SCHEDULE

REDACTED

# BASE LOAD NUCLEAR

NOMINAL 2,234 MW

(Two 1,117 MW Units)

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

The AP1000 is an advanced 1,117 MW nuclear power plant that uses the forces of nature and simplicity of design to enhance plant safety and operations.  The AP1000 Nuclear Steam Supply System (NSSS) plant configuration consists of two Delta−125 steam generators, each connected to the reactor pressure vessel by a single hot leg and two cold legs. There are four reactor coolant pumps that provide circulation of the reactor coolant for heat removal. A pressurizer is connected to one of the hot legs to regulate pressure in the Reactor Coolant System (RCS).  The NSSS is driving a Toshiba type TC6F (52” last row blades) steam turbine, with 1 high pressure and 3 low pressure elements at an operating speed of 1,800 RPM.  Plant cost basis and features include:

One Auxiliary Electric Boiler per unit, 100,000 pounds per hour of saturated steam at 195 psig.

Two, approximately 4,000 KW, Standby Diesel Generators (non-safety related) per unit.

Fuel design is based on the 17x17 XL (14 foot) design used successfully at plants in the U.S. and Europe.

Canned motor reactor coolant pumps, which have been in use by the U.S. Navy for decades.

Circulating water system, including natural draft cooling towers (1 per unit).

Plant systems, structures, and components including the support facilities needed to operate the plant (maintenance shop, offices, training center, warehouses, water intake structures, water-treatment facilities, etc.)

#### State of Technology

The AP1000 design is complete and has been certified by the Nuclear Regulatory Commission for use in the United States.  Combined Operating Licenses have been issued for four AP1000 units at 2 domestic sites - Vogtle (Southern Company), in Georgia and V.C. Summer (SCANA), in South Carolina.  Four AP1000 units are under construction in China and construction activities are under way at the two domestic sites.  Major AP1000 components such as the reactor pressure vessel, steam generators, reactor coolant pumps and passive RHR heat exchangers are currently being fabricated.  Module sub-assemblies, fabricated off-site, are being delivered to the Vogtle site.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

|  | Net Plant Heat Rate Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Condition | REDACTED | REDACTED |
| Annual Average | REDACTED | REDACTED |
| 75% | REDACTED | REDACTED |
| 50% | REDACTED | REDACTED |
| 25% | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Plant will not be used for peaking or for operation at reduced power.

Performance is net to the high side of the GSU and includes station service.

### TOTAL PLANT COSTS

#### Nominal 2234 MW Site (Two 1117 MW Units)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

The cost data is based on both publically available information and information obtained through various discussions with prospective vendors.  This cost data is not accompanied by any degree of vendor guarantee.

Plant costs are overnight costs as of January 2012.

Cost include EPC Contract Price, Owner’s Cost (including licensing and pre-contract activities), and initial fuel core with test energy.

The costs do not include the cost of land estimated at $REDACTED for 2 units.

The initial fuel core cost ($REDACTED) included in the total is based on an 18 month supply. Startup fuel cost for 2 units:  $REDACTED during a 6 month startup.

Estimated test energy credit: $REDACTED.

### O & M COSTS

##### Nominal 2234 MW site (two 1117 MW units):

#### Fixed O&M Costs

###### (Based on the Annual Average Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (For a Nuclear Plant, Variable O&M costs are assumed to be negligible)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

O&M based on new and clean condition output.

Capacity factor of REDACTED%.  Because these are large base load nuclear units, the number of starts per year will be as low as possible.

O&M costs are in January 2012 dollars.

### EMISSIONS

Standby and Ancillary Diesel Generators (Three each per Unit plus 1 security diesel for both units)

| Pollutant Discharged | Lbs (per unit) |
| --- | --- |
| Particulate | REDACTED |
| Sulfur oxide | REDACTED |
| Carbon Monoxide (CO) | REDACTED |
| Hydrocarbons | REDACTED |
| Nitrogen Oxides (NOx) | REDACTED |

#### Basis for Emissions Data:

Four, 4,000 KW generators, non-safety related and four 80 KW Ancillary DGs.

No. 2 Fuel Oil.

Emissions are based on REDACTED for each of the generators per unit.

These emissions estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology will require a more stringent emission limitations than those estimates shown above.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/18 month refueling cycle) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE* - EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) *excludes maintenance outages | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) * Based on new & clean output. | REDACTED for 2234 MW site* |

## TECHNOLOGY FORECAST

#### PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present-2018 | 2018+ |
| --- | --- | --- |
| Representative Technology: | Westinghouse AP1000 GE ESBWR (Economic Simplified Boiling Water Reactor) Areva (Framtome) (Evolutionary Pressurized Water Reactor) | Westinghouse AP1000 GE ESBWR (Economic Simplified Boiling Water Reactor) Areva (Framtome) (Evolutionary Pressurized Water Reactor) Pebble Bed Modular Reactor Small Modular Reactor |
| Average Annual Heat Rate (based on HHV and new & clean conditions) | REDACTED | REDACTED |

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| EXPENDITURE DATA |  |  |  |
| --- | --- | --- | --- |
| Nuclear - 2013 IRP (cash flow) |  |  |  |
| Year | Unit 1 | Unit 2 | Total |
| Year 1 | REDACTED | REDACTED | REDACTED |
| Year 2 | REDACTED | REDACTED | REDACTED |
| Year 3 | REDACTED | REDACTED | REDACTED |
| Year 4 | REDACTED | REDACTED | REDACTED |
| Year 5 | REDACTED | REDACTED | REDACTED |
| Year 6 | REDACTED | REDACTED | REDACTED |
| Year 7 | REDACTED | REDACTED | REDACTED |
| Year 8 | REDACTED | REDACTED | REDACTED |
| Year 9 | REDACTED | REDACTED | REDACTED |
| Year 10 | REDACTED | REDACTED | REDACTED |
| Year 11 | REDACTED | REDACTED | REDACTED |
| Year 12 | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED |

## PROJECT SCHEDULE

REDACTED

BASE LOAD
INTEGRATED GASIFICATION COMBINED CYCLE
OXYGEN BLOWN slagging
nominal 600 mw

## PLANT DESCRIPTION AND DATA SUMMARY1

### GENERAL DESCRIPTION OF THE PLANT

The base load integrated gasification combined cycle unit is a nominally rated 640 MW plant based on a power cycle utilizing two GE 7FB, nominal 232 MW, advanced design industrial combustion turbine generators, two natural circulation heat recovery steam generators (HRSG), a single condensing reheat steam turbine generator and associated support systems.  Coal Gasification is accomplished using two (50%) oxygen-blown GE entrained flow, slurry fed, radiant syngas cooler + quench, slagging gasifier trains.  Traditional (cold) sulfur removal is employed, and nitrogen injection followed by post-combustion SCR is used for NOx control.  The unit is designed for dual fuel operation with coal-derived syngas as the primary fuel and natural gas as the startup and backup fuel (unit will be de-rated on back-up fuel).  An additional gasifier could be installed as a spare where higher reliability is required.

The base load integrated gasification combined cycle unit with carbon capture is a nominally rated 550 MW plant based on a power cycle utilizing two GE 7FB, nominal 232 MW, advanced design industrial combustion turbine generators, two natural circulation heat recovery steam generators (HRSG), a single condensing reheat steam turbine generator and associated support systems.  Coal Gasification is accomplished using two (50%) oxygen-blown GE entrained flow, slurry fed, radiant syngas cooler + quench, slagging gasifier trains.  The carbon monoxide in the raw syngas is shifted to produce syngas rich in hydrogen and carbon dioxide.  Traditional (cold) acid gas removal using the UOP Selexol process is employed, including both sulfur and CO2 removal, and nitrogen injection followed by post-combustion SCR is used for NOx control.  The unit is designed for dual fuel operation with coal-derived syngas as the primary fuel and natural gas as the startup and backup fuel (unit will be de-rated on back-up fuel).  An additional gasifier could be installed as a spare where higher reliability is required.

#### State of Technology

Oxygen-blown gasification technology is commercially available from:

GE Energy

GE Energy acquired the Texaco gasification process and has teamed with Bechtel to offer a reference plant design.  An older version of the GE gasification technology is utilized at the Polk Power Station (Florida), in operation since 1996.  Duke Power has also started construction on a unit in Edwardsport, IN, that will approximately match the description in this document.

ConocoPhillips

ConocoPhillips acquired the Destec gasification process, renaming it E-Gas, and has aligned with Fluor to develop and implement IGCC projects.  The E-gas technology is utilized at the Wabash Power Station (Indiana), in operation since 1996.

Shell

Shell offers the Shell Coal Gasification Process, which is utilized at the Willem Alexander plant (Netherlands), in operation since 1994.

- Krupp Uhde

The Uhde Prenflo technology was developed in cooperation with Shell, but recently Uhde has decided to again market and develop the technology independent of Shell.  The Prenflo technology was selected for the ELCOGAS IGCC (Spain) which has been operating since 1998.

Siemens-Westinghouse

Siemens-Westinghouse acquired the Future Energy (formerly GSP or Noell) gasification technology from Sustec Holding Company in Germany in 2006.  This gasification technology has been in service at the 200 MWth Schwarze Pumpe plant in Germany for the past 20 years.  No commercial plants comparable to those mentioned above are in operation.

Additional installation experience with most of the above gasification technology exists, whether in a power generation or a chemical feedstock application.  As of June, 2008, there were 63 gasification plants in operation worldwide based on the GE Energy technology, although almost all produce chemicals or fuels rather than electricity.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions (without Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### New and Clean Conditions (with Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Basis for Heat Rate Data and Output Data:

The performance and costs are based on Pittsburgh #8 bituminous coal with approximately 2% sulfur.

Average annual condition is defined as a dry bulb temperature of 59°F and
 60% R. H.

GE 7FB Combustion Turbines.

Generic Middle America site (Kenosha, WI), altitude 600 feet above sea level.

- For carbon capture case, CO2 pipeline sulfur spec REDACTED ppmv.

#### Degraded Conditions (without Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Degraded Conditions (with Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Basis for Heat Rate Data and Output Data:

The performance and costs are based on Pittsburgh #8 bituminous coal with approximately 2% sulfur.

Average annual condition is defined as a dry bulb temperature of 59°F and
 60% R. H.

GE 7FB Combustion Turbines.

Generic Middle America site (Kenosha, WI), altitude 600 feet above sea level.

For carbon capture case, CO2 pipeline sulfur spec REDACTED ppmv.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST2

Without Carbon Capture (New and Clean)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

- EPC cost based on the EPRI Total Plant Cost (TPC) basis.

- Includes moderate pre-investment for possible future CO2 capture retrofit.

With Carbon Capture (New and Clean)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

- EPC cost based on the EPRI Total Plant Cost (TPC) basis.

Without Carbon Capture (Degraded)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

- EPC cost based on the EPRI Total Plant Cost (TPC) basis.

- Includes moderate pre-investment for possible future CO2 capture retrofit.

- Degradation of REDACTED% Output and REDACTED% Heat Rate.

With Carbon Capture (Degraded)

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

EPC cost based on the EPRI Total Plant Cost (TPC) basis.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O&M COSTS

#### Fixed O&M Costs (Without Carbon Capture)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Without Carbon Capture)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

- 1st Quarter 2012 dollars.

#### Fixed O&M Costs (With Carbon Capture)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (With Carbon Capture)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

1st Quarter 2012 dollars.

#### Fixed O&M Costs (Without Carbon Capture) (Degraded)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Without Carbon Capture) (Degraded)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

- 1st Quarter 2012 dollars.

- Degradation of REDACTED% Output and REDACTED% Heat Rate.

#### Fixed O&M Costs (With Carbon Capture) (Degraded)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (With Carbon Capture) (Degraded)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

1st Quarter 2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

Without Carbon Capture (New and Clean)

|  | Concentration | lb/MWh |
| --- | --- | --- |
| Sulfur Oxides (SOX) | REDACTED | REDACTED |
| Nitrogen Oxides (NOX) | REDACTED | REDACTED |
| Particulate Matter (PM - filterable) | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED |
| Carbon Dioxide (CO2) | REDACTED | REDACTED |

#### Basis for Emissions Data:

Post combustion control of NOX using SCR is assumed.

PM emissions source is primarily from air intake to the CT.

With Carbon Capture (New and Clean)

|  | Concentration | lb/MWh |
| --- | --- | --- |
| Sulfur Oxides (SOX) | REDACTED | REDACTED |
| Nitrogen Oxides (NOX) | REDACTED | REDACTED |
| Particulate Matter (PM - filterable) | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED |
| Carbon Dioxide (CO2) | REDACTED | REDACTED |

#### Basis for Emissions Data:

Post combustion control of NOX using SCR is assumed.

PM emissions source is primarily from air intake to the CT.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE – EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) * Based on no spare gasifier and no backup fuel ** Based on no spare gasifier with unlimited supply of backup fuel (natural gas) | REDACTED* REDACTED** |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) * Based on the assumption that an LTSA is in place for the Combined Cycle combustion turbines, due to extended lifetime requiring substantial capital replacements of combustion turbines. [Degraded values in brackets] | REDACTED* (without CCS) REDACTED* (with CCS) |

1The information in this document is based primarily on Integrated Gasification Combined Cycle (IGCC) Design Considerations for Carbon Dioxide (CO2) Capture: Engineering and Economic Assessment of Integrated Gasification Combined Cycle Coal Power Plants for Near-Term Deployment. EPRI, Palo Alto, CA: 2009. 1015690

2The total plant costs for the GE gasification technology reported by Duke Energy Indiana in the Edwardsport IGCC project filing with the Indiana Utility Regulatory Commission are approximately 10% higher than the costs reported here from the above EPRI report for the same technology.

TECHNOLOGY FORECAST

#### PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present to 2015 |
| --- | --- |
| Representative Technology | "F"-IGCC Oxygen blown gasifier to produce low-BTU fuel gas and steam (7FB CT) |
| Average Annual Heat Rate (based on HHV) | REDACTED Btu/kWh (without CCS) REDACTED Btu/kWh (with CCS) |

Notes:

Unable to project beyond 2015.

## Expenditure data

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| Year |  | Percent |
| --- | --- | --- |
| 1 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 2 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 3 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 4 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 5 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 6 | First Half | REDACTED |
|  | Second Half | REDACTED |
| 7 | First Half | REDACTED |
|  | Second Half | REDACTED |
| Total |  | 100.0% |

## indicative project schedule

REDACTED

BASE LOAD INTEGRATED GASIFICATION COMBINED CYCLE AIR BLOWN NOMINAL 600 MW

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

The base load integrated gasification combined cycle unit is a nominally rated 600 MW plant based on a power cycle utilizing two GE 7FB, nominal 232 MW, advanced design industrial combustion turbine generators, two natural circulation heat recovery steam generators (HRSG), a single condensing reheat steam turbine generator and associated support systems.  Coal Gasification is accomplished using two (50%) air-blown Transport Gasifier trains.  The carbon monoxide in the raw syngas is shifted to produce syngas rich in hydrogen and carbon dioxide.  Traditional (cold) acid gas removal using the UOP Selexol process is employed, including both sulfur and CO2 removal.  Ammonia, mercury, and other contaminants are also removed from the syngas at low temperature before it is combusted in the gas turbines.  NOx can be controlled without the use of selective catalytic reduction (SCR) in the HRSG, but SCR is assumed for this data for even lower NOx.  The unit is designed for dual fuel operation with syngas derived from PRB coal as the primary fuel and natural gas as the startup and backup fuel.

State of Technology

The gasification technology selected as the basis for this data was developed by Southern Company at the 48 tpd DOE Power Systems Development Facility.  The first commercial unit is expected to achieve commercial operation in 2012 in DongGuan, China.  This IGCC unit will have a capacity of about 113 MW and will be integrated with an existing combined cycle plant.  Another unit is being designed for the Kemper County IGCC Project (KCIP) at Mississippi Power Company (MPC).  The KCIP is a two-on-one IGCC (nominal 600 MW) that is scheduled for start-up in 2014 and is designed to use locally mined lignite as the primary fuel.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions (without Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### New and Clean Conditions (with Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Basis for Heat Rate Data and Output Data:

The performance and costs are based on Montana Rosebud Powder River Basin (PRB) sub-bituminous coal with less than 1% sulfur.

Average annual condition is defined as a dry bulb temperature of 65°F and
 73% R. H.

GE 7FB Combustion Turbines.

Generic Southeast site, altitude 218 feet above sea level.

- CO2 pipeline sulfur spec REDACTED ppmw.

#### Degraded Conditions (without Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Degraded Conditions (with Carbon Capture):

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Average Annual Condition | REDACTED | REDACTED |

#### Basis for Heat Rate Data and Output Data:

The performance and costs are based on Montana Rosebud Powder River Basin (PRB) sub-bituminous coal with less than 1% sulfur.

Average annual condition is defined as a dry bulb temperature of 65°F and
 73% R. H.

GE 7FB Combustion Turbines.

Generic Southeast site, altitude 218 feet above sea level.

CO2 pipeline sulfur spec REDACTED ppmw.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

New and Clean

| Without Carbon Capture | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

| With Carbon Capture | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

- EPC cost based on the EPRI Total Plant Cost (TPC) basis.

Degraded

| Without Carbon Capture | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

| With Carbon Capture | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW is based on the average annual condition (peak rating not available).

Generic “Greenfield” site.

Plant costs are overnight costs as of 1st Quarter 2012.

- EPC cost based on the EPRI Total Plant Cost (TPC) basis.

- Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O&M COSTS

#### Fixed O&M Costs (Without Carbon Capture)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Without Carbon Capture)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Fixed O&M Costs (With Carbon Capture)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (With Carbon Capture)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

1st Quarter 2012 dollars.

- Variable O&M includes credit of $REDACTED for ammonia sales.

#### Fixed O&M Costs (Without Carbon Capture) (Degraded)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Without Carbon Capture) (Degraded)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Fixed O&M Costs (With Carbon Capture) (Degraded)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (With Carbon Capture) (Degraded)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.  REDACTED starts per year.

1st Quarter 2012 dollars.

Variable O&M includes credit of $REDACTED for ammonia sales.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

Without Carbon Capture (New and Clean)

|  | Concentration | lb/MWh |
| --- | --- | --- |
| Sulfur Oxides (SOX) | REDACTED | REDACTED |
| Nitrogen Oxides (NOX) | REDACTED | REDACTED |
| Particulate Matter (PM - filterable) | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED |
| Carbon Dioxide (CO2) | REDACTED | REDACTED |

#### Basis for Emissions Data:

Post combustion control of NOX using SCR is assumed.

PM emissions source is primarily from air intake to the CT.

With Carbon Capture (New and Clean)

|  | Concentration | lb/MWh |
| --- | --- | --- |
| Sulfur Oxides (SOX) | REDACTED | REDACTED |
| Nitrogen Oxides (NOX) | REDACTED | REDACTED |
| Particulate Matter (PM - filterable) | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED |
| Carbon Dioxide (CO2) | REDACTED | REDACTED |

#### Basis for Emissions Data:

Post combustion control of NOX using SCR is assumed.

PM emissions source is primarily from air intake to the CT.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE – EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED | Yes |
| ### PROJECT SCHEDULE ATTACHED | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) * Based on the assumption that an LTSA is in place for the Combined Cycle combustion turbines, due to extended lifetime requiring substantial capital replacements of combustion turbines. [Degraded values in brackets] | REDACTED (without CCS) REDACTED (with CCS)* |

## TECHNOLOGY FORECAST

#### PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present to 2015 |
| --- | --- |
| Representative Technology | 7FB TrIG Air-blown gasifier to produce low-BTU fuel gas and steam |
| Average Annual Heat Rate (based on HHV) | REDACTED Btu/kWh (without CCS) REDACTED Btu/kWh (with CCS) |

Notes:

Unable to project beyond 2015.

## expenditure Data

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| Months prior to COD | Percent |
| --- | --- |
| -79 | REDACTED |
| -78 | REDACTED |
| -77 | REDACTED |
| -76 | REDACTED |
| -75 | REDACTED |
| -74 | REDACTED |
| -73 | REDACTED |
| -72 | REDACTED |
| -71 | REDACTED |
| -70 | REDACTED |
| -69 | REDACTED |
| -68 | REDACTED |
| -67 | REDACTED |
| -66 | REDACTED |
| -65 | REDACTED |
| -64 | REDACTED |
| -63 | REDACTED |
| -62 | REDACTED |
| -61 | REDACTED |
| -60 | REDACTED |
| -59 | REDACTED |
| -58 | REDACTED |
| -57 | REDACTED |
| -56 | REDACTED |
| -55 | REDACTED |
| -54 | REDACTED |
| -53 | REDACTED |
| -52 | REDACTED |
| -51 | REDACTED |
| -50 | REDACTED |
| -49 | REDACTED |
| -48 | REDACTED |
| -47 | REDACTED |
| -46 | REDACTED |
| -45 | REDACTED |
| -44 | REDACTED |
| -43 | REDACTED |
| -42 | REDACTED |
| -41 | REDACTED |
| -40 | REDACTED |
| -39 | REDACTED |
| -38 | REDACTED |
| -37 | REDACTED |
| -36 | REDACTED |
| -35 | REDACTED |
| -34 | REDACTED |
| -33 | REDACTED |
| -32 | REDACTED |
| -31 | REDACTED |
| -30 | REDACTED |
| -29 | REDACTED |
| -28 | REDACTED |
| -27 | REDACTED |
| -26 | REDACTED |
| -25 | REDACTED |
| -24 | REDACTED |
| -23 | REDACTED |
| -22 | REDACTED |
| -21 | REDACTED |
| -20 | REDACTED |
| -19 | REDACTED |
| -18 | REDACTED |
| -17 | REDACTED |
| -16 | REDACTED |
| -15 | REDACTED |
| -14 | REDACTED |
| -13 | REDACTED |
| -12 | REDACTED |
| -11 | REDACTED |
| -10 | REDACTED |
| -9 | REDACTED |
| -8 | REDACTED |
| -7 | REDACTED |
| -6 | REDACTED |
| -5 | REDACTED |
| -4 | REDACTED |
| -3 | REDACTED |
| -2 | REDACTED |
| -1 | REDACTED |
| Total | 100.00% |

## indicative project schedule (No carbon capture)

REDACTED

BASE / INTERMEDIATE LOAD NATURAL GAS ONLY COMBINED CYCLE “G” & “H” TECHNOLOGY

NOMINAL 850 MW UNIT AND NOMINAL 930 MW UNIT

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The base / intermediate load combined cycle unit is assumed to be located at a generic “Greenfield” site and is nominally rated 850 MW or 930 MW at summer peaking conditions (95 °F ambient, fired).  Each unit utilizes two (2) "G"-class, advanced design industrial combustion turbine-generators with evaporative coolers, two natural circulation triple pressure heat recovery steam generators (HRSGs) with reheat sections and integral deaerators, a single condensing reheat steam turbine, a steam condenser with a mechanical draft cooling tower system for condenser cooling and associated support systems.  The combustion turbine will be housed in an individual weatherproof outdoor enclosure, which includes insulation for sound attenuation and thermal protection.

###### The primary difference between the “F” and the “G” combined cycle designs is that the “G” design provides greater thermodynamic integration of the cycle.  The M501G1+ CT uses intermediate pressure steam from the HRSG to cool the combustors and returns hotter steam to the boiler reheater for supply to the IP steam turbine.  In addition, rejected heat from the gas turbine rotor is used to supply energy to the cycle’s feed water heating circuit.  The “501G1+” machines are nominally rated at 267 MW at 65°F (compared to ~200 MW for the “F”).  The M501GAC machine is very similar to the M501G1+ machine.  The primary difference is the absence of combustor steam cooling and the slightly improved output as a result of improved thermal coatings.  In almost all other respects, the machines are identical.  The 501GAC is rated nominally at 269 MW at 65°F.

###### The two different output levels represented by the units are the result of a different level of duct firing in the HRSG and a larger steam turbine.  The M501G1+ CT could be configured in a similar fashion to the 501GAC based plant (900+ MW), but with a slightly lower output.

###### In addition, the GAC-based plant design is capable of utilizing a Siemens 
SGT6-8000H turbine in place of the 501GAC.  The performance differences for this exchange are relatively small, as are the costs.  Therefore, only the 501GAC data is shown.  Other differences such as long term maintenance agreements could vary the cost delta between the two turbines from one project to another.

#### State of Technology

###### The 501G1+ technology is currently available.  The 501GAC and 8000H have no commercial units in the US as of this time, but are in production.

### HEAT RATE AND OUTPUT DATA

#### M501G1+

#### New and Clean Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @~60% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ 75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.

#### M501GAC

#### New and Clean Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @~50% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ 75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.
M501G1+

#### Degraded Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @~60% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ 75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

#### M501GAC

#### Degraded Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @~50% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ 75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

#### M501G1+

#### Nominal 850 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### M501GAC

#### Nominal 930 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1860 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### M501G1+

#### Nominal 850 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

#### M501GAC

#### Nominal 930 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1860 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 850 MW site (1 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1700 MW site (2 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 930 MW site (1 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1860 MW site (2 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 850 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1700 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

##### Nominal 930 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1860 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

M501G1+ (New and Clean)

| Emissions (Natural Gas) | ppm | lb/hr | lb/MMBtu |
| --- | --- | --- | --- |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) with SCR | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM) – Filterable | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM) – Condensable | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) with Catalyst | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC) with Catalyst | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

- Emissions values reflect firing natural gas at REDACTED°F, REDACTED% load, and duct firing REDACTED MMBtu/hr – HHV of natural gas (Worst Case).

A Condensable/Filterable ratio of REDACTED was used to find condensable Particulate emissions.

Fuel gas heating is to REDACTEDF.

- lb/MMBtu based on using REDACTED MMBtu/hr - HHV in the gas turbine plus the REDACTED MMBtu/hr - HHV supplied in the duct burner for a total of REDACTED MMBtu/hr – HHV.

- Duct burner exhaust constituents estimated with GateCycle model including conceptual HRSG, STG, and BOP.

- Duct burner NOx estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Duct burner CO estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Duct burner VOC as CH4 estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Assumes an emission factor of REDACTED lb SO2 per million scf from EPA AP-42 document.

- Natural Gas composition based on SCS spec for “G” gas turbines, January 2006.

M501GAC (New and Clean)-

| Emissions (Natural Gas) | ppm | lb/hr | lb/MMBtu |
| --- | --- | --- | --- |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) with SCR | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM10 Front and Back Half) | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) with Catalyst | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC) with Catalyst | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

- Natural gas emissions values reflect REDACTED°F ambient temperature, REDACTED% load, and duct firing REDACTED MMBtu/hr – HHV of natural gas.

- Duct burner exhaust constituents estimated with GateCycle model including conceptual HRSG, STG, and BOP.

- Duct burner NOx estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Duct burner CO estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Duct burner VOC as CH4 estimated at REDACTED lb/MMBtu – HHV based on past projects.

- Calculations use data provided by MHI at a site elevation of 200ft.

- Values assume NOx reduction through the SCR and CO and VOC reduction through the oxidation catalyst.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE – EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for 850 MW site REDACTED for 1700 MW site REDACTED for 930 MW site REDACTED for 1860 MW site |

## TECHNOLOGY FORECAST

PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present-2015 | 2015+ |
| --- | --- | --- |
| Representative Technology: | 501G1+ or 501GAC | 501GAC or Siemens H |
| Average Annual Heat Rate (based on HHV) | REDACTED (G1+) or REDACTED (GAC) | REDACTED |

Performance estimates based on the expected future technological advances.

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| G-Class (Gas Only) |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |

## INDICATIVE PROJECT SCHEDULE

REDACTED

BASE / INTERMEDIATE LOAD DUAL FUEL COMBINED CYCLE “G” & “H” TECHNOLOGY NOMINAL 850 MW UNIT AND NOMINAL 930 MW UNIT

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The base / intermediate load combined cycle unit is assumed to be located at a generic “Greenfield” site and is nominally rated 850 MW or 930 MW at summer peaking conditions (95 °F ambient, fired).  Each unit utilizes two (2) "G"-class, advanced design industrial combustion turbine-generators with evaporative coolers, two natural circulation triple pressure heat recovery steam generators (HRSGs) with reheat sections and integral deaerators, a single condensing reheat steam turbine, a steam condenser with a mechanical draft cooling tower system for condenser cooling and associated support systems.  The combustion turbine will be housed in an individual weatherproof outdoor enclosure, which includes insulation for sound attenuation and thermal protection.

###### The primary difference between the “F” and the “G” combined cycle designs is that the “G” design provides greater thermodynamic integration of the cycle.  The M501G1+ CT uses intermediate pressure steam from the HRSG to cool the combustor and returns hotter steam to the boiler reheater for supply to the IP steam turbine.  In addition, rejected heat from the gas turbine rotor is used to supply energy to the cycle’s feed water heating circuit.  The “501G1+” machines are nominally rated at 267 MW at 65°F (compared to ~200 MW for the “F”). The M501GAC machine is very similar to the M501G1+ machine.  The primary difference is the absence of combustor steam cooling and the slightly improved output as a result of improved thermal coatings.  In almost all other respects, the machines are identical.  The 501GAC is rated nominally at 269 MW at 65°F.

###### The two different output levels represented by the units are the result of a different level of duct firing in the HRSG and a larger steam turbine.  The M501G1+ CT could be configured in a similar fashion to the 501GAC based plant (900+ MW), but with a slightly lower output.

###### In addition, the GAC-based plant design is capable of utilizing a Siemens 
SGT6-8000H turbine in place of the 501GAC.  The performance differences for this exchange are relatively small, as are the costs.  Therefore, only the 501GAC data is shown.  Other differences such as long term maintenance agreements could vary the cost delta between the two turbines from one project to another.

#### State of Technology

###### The 501G1+ technology is currently available.  The 501GAC and Siemens 8000H have no installed units in the US as of this time, but are in production.

### HEAT RATE AND OUTPUT DATA

#### M501G1+

#### New and Clean Conditions:

Natural gas performance is identical to the natural gas only “G1+” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Use of evaporative coolers is not permitted while operating on fuel oil.

Performance is net to the high side of the GSU and includes station service.

#2 Distillate oil fuel.

Fuel oil heating to REDACTEDF.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.

#### M501GAC

#### New and Clean Conditions:

Natural gas performance is identical to the natural gas only “GAC” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Use of evaporative coolers is not permitted while operating on fuel oil.

Performance is net to the high side of the GSU and includes station service

#2 Distillate oil fuel.

Fuel oil heating to REDACTEDF.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.
M501G1+

#### Degraded Conditions:

Natural gas performance is identical to the natural gas only “G1+” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Use of evaporative coolers is not permitted while operating on fuel oil.

Performance is net to the high side of the GSU and includes station service.

#2 Distillate oil fuel.

Fuel Oil heating to REDACTEDF.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.

#### M501GAC

#### Degraded Conditions:

Natural gas performance is identical to the natural gas only “GAC” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Use of evaporative coolers is not permitted while operating on fuel oil.

Performance is net to the high side of the GSU and includes station service.

#2 Distillate oil fuel.

Fuel oil heating to REDACTEDF.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.

### TOTAL PLANT COST

#### M501G1+

#### Nominal 850 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### M501GAC

#### Nominal 930 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1860 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### M501G1+

#### Nominal 850 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1700 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

#### M501GAC

#### Nominal 930 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1860 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 850 MW site (1 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1700 MW site (2 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 930 MW site (1 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1860 MW site (2 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 850 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1700 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

##### Nominal 930 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1860 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

M501G1+ (New and Clean)

| Emissions | ppm | lb/hr | lb/MMBtu |
| --- | --- | --- | --- |
| Sulfur Dioxide (SO2) | - | - | - |
| Nitrogen Oxides (NOx) with SCR | - | - | - |
| Particulate Matter (PM10 Front and Back Half) | - | - | - |
| Carbon Monoxide (CO) with Catalyst | - | - | - |
| Volatile Organics (VOC) with Catalyst | - | - | - |

#### Basis for Emissions Data:

- Oil fired emissions not available for the 2x1 configuration M501G1+.

M501GAC (New and Clean)

| Emissions (Oil Fired) | ppm | lb/hr | lb/MMBtu |
| --- | --- | --- | --- |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) with SCR | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM10 Front and Back Half) | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) with Catalyst | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC) with Catalyst | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

- Calculations use data provided by MHI at a site elevation of 200ft.

- Oil emissions values reflect REDACTED°F ambient temperature, REDACTED% load, no duct firing, and no evaporative cooler.

- Values assume NOx reduction through the SCR and CO and VOC reduction through the oxidation catalyst.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE – EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for 850 MW site REDACTED for 1700 MW site REDACTED for 930 MW site REDACTED for 1860 MW site |

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| G-Class (Dual Fuel) |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |

## INDICATIVE PROJECT SCHEDULE

REDACTED

BASE / INTERMEDIATE LOAD NATURAL GAS ONLY COMBINED CYCLE “F” TECHNOLOGY

NOMINAL 750 MW UNIT

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The base / intermediate load combined cycle unit is assumed to be located at a generic “Greenfield” site and is nominally rated 750 MW at the summer peaking conditions. Each unit is based on a power cycle utilizing two (2) "F"-class, advanced design industrial combustion turbine-generators with evaporative coolers, two natural circulation triple pressure heat recovery steam generators (HRSGs) with reheat sections and integral deaerators, a single condensing reheat steam turbine, a steam condenser with a mechanical draft cooling tower system for condenser cooling and associated support systems.  The combustion turbine will be housed in an individual weatherproof outdoor enclosure, which includes insulation for sound attenuation and thermal protection.

###### The primary difference between the “F” and the “G” combined cycle designs is that the “G” design provides greater thermodynamic integration of the cycle.  The “G” CT uses intermediate pressure steam from the HRSG to cool the combustor and returns hotter steam to the boiler reheater for supply to the IP steam turbine.  In addition, rejected heat from the gas turbine compressor is used to supply energy to the cycle’s feed water heating circuit.  The “G” machines are nominally rated at 267 MW @ISO conditions (compared to ~200 MW for the “F”).

###### The SGT6-5000F4 has one row of inlet guide vanes, a 13-stage high efficiency axial compressor with three stages of variable internal guide vanes, an integral gas chamber equipped with 16 can-annular combustors arranged in a circular array, and a 4-stage reaction type turbine.  This gas turbine is capable of power augmentation (also known as “steam injection”) for additional power when needed.

#### State of Technology

###### This technology is currently available.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @ ~60% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ ~75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation @ 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| PA/FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.

Peak rating is based on maximum steam injection ratio for power augmentation.

#### Degraded Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Minimum @ ~60% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Intermediate @ ~75% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation @ 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |
| PA/FP @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above 59°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

Natural gas fuel (assumed natural gas compressor not required) with fuel gas heating to REDACTEDF.

Peak rating is based on maximum steam injection ratio for power augmentation.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

#### Nominal 750 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1500 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating and includes.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### Nominal 750 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1500 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating and includes.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 750 MW site (1 x 2-on-1):

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1500 MW site (2 x 2-on-1):

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.
.

##### Nominal 750 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1500 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

New and Clean (Natural Gas)

|  | Natural Gas |  |  |
| --- | --- | --- | --- |
|  | ppmvd @15%O2 | lb/hr | lb/MMBtu - HHV |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) with SCR | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM10 Front & Back Half) | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) with catalyst | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC) with catalyst | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

- PM values are per US EPA Method 5/202 (front and back half).

- Duct burner exhaust constituents estimated with GateCycle model including conceptual HRSG, STG, and BOP.

- Duct burner NOx estimated at REDACTED lb/MMBtu – HHW based on past projects.

- Duct burner CO estimated REDACTED lb/MMBtu – HHV based on past projects.

Duct burner VOC as CH4 estimated at REDACTED lb/MMBtu – HHV based on past projects.

Based on Siemens F4 Ultra Low NOx Combustor data at a 200ft elevation.

Natural gas emissions values reflect REDACTED°F ambient temperature, REDACTED% load, and duct firing REDACTED MMBtu/hr – HHV of natural gas.

Values assume NOx reduction through the SCR and CO and VOC reduction through the oxidation catalyst.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE –EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for 750 MW site REDACTED for 1500 MW site |

## TECHNOLOGY FORECAST

PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present-2015 | 2015+ |
| --- | --- | --- |
| Representative Technology: | Siemens F4 | F class (enhanced) |
| Average Annual Heat Rate (based on HHV) | REDACTED | REDACTED |

Performance estimates based on the expected future technological advances with the understanding that the “F” technology is approaching a mature state.

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| F-Class (Gas Only) |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |

## indicative project schedule

REDACTED

BASE / INTERMEDIATE LOAD DUAL FUEL COMBINED CYCLE “F” TECHNOLOGY NOMINAL 750 MW UNIT

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The base / intermediate load combined cycle unit is assumed to be located at a generic “Greenfield” site and is nominally rated 750 MW at the summer peaking conditions. Each unit is based on a power cycle utilizing two (2) "F"-class, advanced design industrial combustion turbine-generators with evaporative coolers, two natural circulation triple pressure heat recovery steam generators (HRSGs) with reheat sections and integral deaerators, a single condensing reheat steam turbine, a steam condenser with a mechanical draft cooling tower system for condenser cooling and associated support systems.  The combustion turbine will be housed in an individual weatherproof outdoor enclosure, which includes insulation for sound attenuation and thermal protection.

###### The primary difference between the “F” and the “G” combined cycle designs is that the “G” design provides greater thermodynamic integration of the cycle.  The “G” CT uses intermediate pressure steam from the HRSG to cool the combustor and returns hotter steam to the boiler reheater for supply to the IP steam turbine.  In addition, rejected heat from the gas turbine compressor is used to supply energy to the cycle’s feed water heating circuit.  The “G” machines are nominally rated at 267 MW @ISO conditions (compared to ~200 MW for the “F”).

###### The SGT6-5000F4 has one row of inlet guide vanes, a 13-stage high efficiency axial compressor with three stages of variable internal guide vanes, an integral gas chamber equipped with 16 can-annular combustors arranged in a circular array, and a 4-stage reaction type turbine.   This gas turbine is capable of power augmentation (also known as “steam injection”) for additional power when needed.

#### State of Technology

###### This technology is currently available.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

Natural gas performance is identical to the natural gas only “F” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation @ 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above REDACTED°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

#2 Distillate oil fuel.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.

#### Degraded Conditions:

Natural gas performance is identical to the natural gas only “F” technology.

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Normal Operation @ 100% CT Load Average Annual Conditions | REDACTED | REDACTED |
| Normal Operation @ 100% CT Load Peaking Conditions | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Peaking condition is defined as a dry bulb temperature of 95°F and 45% R. H.

Average annual condition is defined as a dry bulb temperature of 65°F and
 75% R. H.

185 ft site elevation (200 ft to CT centerline).

Unit output is for one 2-on-1 site.

Evaporative cooler in use above REDACTED°F with REDACTED% effectiveness.

Performance is net to the high side of the GSU and includes station service.

#2 Distillate oil fuel.

Performance guarantees are not provided by the manufacturers for oil operation unless requested.  Overall plant performance estimates are therefore less accurate than on gas.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

#### Nominal 750 MW Site (1 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1500 MW Site (2 x 2-on-1) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating and includes.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### Nominal 750 MW Site (1 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 1500 MW Site (2 x 2-on-1) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Cost per kW based on the peaking rating and includes.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 750 MW site (1 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1500 MW site (2 x 2-on-1):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.
.

##### Nominal 750 MW site (1 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### nominal 1500 MW site (2 x 2-on-1):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Average Annual Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on maintenance work being self performed.

Capacity factor of REDACTED%. REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

New and Clean (Oil Fired)

|  | Fuel Oil |  |  |
| --- | --- | --- | --- |
|  | ppmvd @15%O2 | lb/hr | lb/MMBtu - HHV |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) with SCR | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM10 Front & Back Half) | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) with catalyst | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC) with catalyst | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

PM values are per US EPA Method 5/202 (front and back half).

Based on Siemens F4 Ultra Low NOx Combustor data at 200ft elevation.

- Oil emissions values reflect REDACTED°F ambient temperature, REDACTED% load, no duct firing.

- Values assume NOx reduction through the SCR and CO and VOC reduction through the oxidation catalyst.

- Natural gas emissions for a dual fuel capable machine are identical to those of a gas only CT.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT UNPLANNED OUTAGE RATE - EUOR (%) (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for 750 MW site REDACTED for 1500 MW site |

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| F-Class (Dual Fuel) |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |

## indicative project schedule

REDACTED

PEAKING NATURAL GAS SIMPLE CYCLE COMBUSTION TURBINE “F” TECHNOLOGY NOMINAL 350 MW

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### These simple cycle units are assumed to be located at a generic “Greenfield” site.  The model consists of two (2) Siemens SGT6-5000F4 advanced design industrial combustion turbine-generators nominally rated at 185 MW each (for 9 ppm combustor at F3 firing temperature).  Extensive factory modularization of systems and components results in low costs for peaking applications.  The units utilize natural gas only. NOx is controlled to 9 ppm by dry low NOx combustors.

###### The SGT6-5000F4 has one row of inlet guide vanes, a 13-stage high efficiency axial compressor with three stages of variable internal guide vanes, an integral gas chamber equipped with 16 can-annular combustors arranged in a circular array, and a 4-stage reaction type turbine.  The compressor for this machine is redesigned from the FD3 and integrates the best features from the Siemens’ pedigree engines and the former Westinghouse product line, providing the 5000F4 with additional power output and improved efficiencies at base and part load.

#### State of Technology

###### This peaking unit will utilize mature technology that is commercially available at the present time.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Output, Gas | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

DB = 95 °F; 45% R. H.

Performance shown is for two Siemens SGT6-5000F4 units.

Altitude is 200 Feet above Sea Level.

Evaporative Cooler with REDACTED% Effectiveness.

Performance is net to the high side of the GSU and includes station service.

#### Degraded Conditions:

| Gas Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Output, Gas | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

DB = 95 °F; 45% R. H.

Performance shown is for two Siemens SGT6-5000F4 units.

Altitude is 200 Feet above Sea Level.

Evaporative Cooler with REDACTED% Effectiveness.

Performance is net to the high side of the GSU and includes station service.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

#### Nominal 350 MW Site (2 x F4) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 700 MW Site (4 x F4) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Cost:

Cost per kW based on gas-fired performance.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED for 2x5000F4 and $REDACTED for 4x5000F4 is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

#### Nominal 350 MW Site (2 x F4) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 700 MW Site (4 x F4) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Cost:

Cost per kW based on gas-fired performance.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED for 2x5000F4 and $REDACTED for 4x5000F4 is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 350 MW site:

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 700 MW site (4 x F4):

#### Fixed O&M Costs

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on self performing maintenance work.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 350 MW site:

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 700 MW site (4 x F4):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on self performing maintenance work.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

New and Clean

See Dual Fuel Natural Gas Emissions.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### DEMAND EQUIVALENT FORCED OUTAGE RATE - EFORd (%) (The probability that the unit will not produce power when demanded.) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | GAS Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for a 350 MW site and REDACTED for a 700 MW site |

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| ## F-Class (Gas Only) Two Unit |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |  |
| 1 | REDACTED | REDACTED |  |
| 2 | REDACTED | REDACTED |  |
| 3 | REDACTED | REDACTED |  |
| 4 | REDACTED | REDACTED |  |
| 5 | REDACTED | REDACTED |  |
| 6 | REDACTED | REDACTED |  |
| 7 | REDACTED | REDACTED |  |
| 8 | REDACTED | REDACTED |  |
| 9 | REDACTED | REDACTED |  |
| 10 | REDACTED | REDACTED |  |
| 11 | REDACTED | REDACTED |  |
| 12 | REDACTED | REDACTED |  |
| 13 | REDACTED | REDACTED |  |
| 14 | REDACTED | REDACTED |  |
| 15 | REDACTED | REDACTED |  |
| 16 | REDACTED | REDACTED |  |
| 17 | REDACTED | REDACTED |  |
| 18 | REDACTED | REDACTED |  |
| 19 | REDACTED | REDACTED |  |
| 20 | REDACTED | REDACTED |  |
| 21 | REDACTED | REDACTED |  |
| 22 | REDACTED | REDACTED |  |
| 23 | REDACTED | REDACTED |  |
| 24 | REDACTED | REDACTED |  |
| 25 | REDACTED | REDACTED |  |
| 26 | REDACTED | REDACTED |  |
| 27 | REDACTED | REDACTED |  |
| 28 | REDACTED | REDACTED |  |
| 29 | REDACTED | REDACTED |  |
| 30 | REDACTED | REDACTED |  |
| 31 | REDACTED | REDACTED |  |
| 32 | REDACTED | REDACTED |  |
| 33 | REDACTED | REDACTED |  |
| 34 | REDACTED | REDACTED |  |
| 35 | REDACTED | REDACTED |  |
| 36 | REDACTED | REDACTED |  |
| 37 | REDACTED | REDACTED |  |
| 38 | REDACTED | REDACTED |  |
| 39 | REDACTED | REDACTED |  |
| 40 | REDACTED | REDACTED |  |
| 41 | REDACTED | REDACTED |  |
| 42 | REDACTED | REDACTED |  |
| 43 | REDACTED | REDACTED |  |
| 44 | REDACTED | REDACTED |  |
| 45 | REDACTED | REDACTED |  |
| 46 | REDACTED | REDACTED |  |
| 47 | REDACTED | REDACTED |  |
| 48 | REDACTED | REDACTED |  |
| 49 | REDACTED | REDACTED |  |
| 50 | REDACTED | REDACTED |  |

| F-Class (Gas Only) Four Unit |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |

## INDICATIVE PROJECT SCHEDULE

REDACTED

## INDICATIVE PROJECT SCHEDULE

REDACTED

PEAKING DUAL-FUEL SIMPLE CYCLE COMBUSTION TURBINE “F” TECHNOLOGY NOMINAL 350 MW

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### These simple cycle units are assumed to be located at a generic “Greenfield” site.  The model consists of two (2) Siemens SGT6-5000F4 advanced design industrial combustion turbine-generators nominally rated at 185 MW each (for 9 ppm combustor at F3 firing temperature).  Extensive factory modularization of systems and components results in low costs for peaking applications.  The units may either utilize natural gas or No. 2 distillate fuel. NOx is controlled to 9 ppm on natural gas by dry low NOx combustors and 42-ppm on No. 2 distillate using water injection.

###### The SGT6-5000F4 has one row of inlet guide vanes, a 13-stage high efficiency axial compressor with three stages of variable internal guide vanes, an integral gas chamber equipped with 16 can-annular combustors arranged in a circular array, and a 4-stage reaction type turbine.  The compressor for this machine is redesigned from the FD3 and integrates the best features from the Siemens’ pedigree engines and the former Westinghouse product line, providing the 5000F4 with additional power output and improved efficiencies at base and part load.

#### State of Technology

###### This peaking unit will utilize mature technology that is commercially available at the present time.

### HEAT RATE AND OUTPUT DATA

#### New and Clean Conditions:

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Output, Oil* | REDACTED | REDACTED |

#### * See the previous section for performance data for operation on Natural Gas

#### Basis for Heat Rate and Output Data:

Natural gas performance for the dual fuel peaking unit is identical to the performance for the natural gas only unit.

DB = 95 °F; 45% R. H.

Performance shown is for two Siemens SGT6-5000F4 units.

Altitude is 200 Feet above Sea Level.

Evaporative Cooler with REDACTED% Effectiveness.

#2 Distillate oil fuel.

Performance is net to the high side of the GSU and includes station service.

#### Degraded Conditions:

| Oil Operation | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Peaking Output, Oil* | REDACTED | REDACTED |

#### * See the previous section for performance data for operation on Natural Gas

#### Basis for Heat Rate and Output Data:

Natural gas performance for the dual fuel peaking unit is identical to the performance for the natural gas only unit.

DB = 95 °F; 45% R. H.

Performance shown is for two Siemens SGT6-5000F4 units.

Altitude is 200 Feet above Sea Level.

Evaporative Cooler with REDACTED% Effectiveness.

#2 Distillate oil fuel.

Performance is net to the high side of the GSU and includes station service.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### TOTAL PLANT COST

#### Nominal 350 MW Site (2 x F4) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 700 MW Site (4 x F4) (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Cost:

Cost per kW based on gas-fired performance.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED for 2x5000F4 and $REDACTED for 4x5000F4 is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

- Nominal 350 MW Site (2 x F4) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Nominal 700 MW Site (4 x F4) (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC Cost | REDACTED | REDACTED |
| Site Cost | REDACTED | REDACTED |
| Owner's Cost | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Cost:

Cost per kW based on gas-fired performance.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

$REDACTED for 2x5000F4 and $REDACTED for 4x5000F4 is included in the site cost for land.

The plant costs are overnight costs as of 1/1/12.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### O & M COSTS

##### Nominal 350 MW site:

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 700 MW site (4 x F4):

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on self performing maintenance work.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 350 MW site:

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

##### Nominal 700 MW site (4 x F4):

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Based on self performing maintenance work.

Capacity factor of REDACTED%.  REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### EMISSIONS

New and Clean

|  | Gas |  |  | Oil |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | ppmvd @15% O2 | lb/hr | lb/MMBtu -HHV | ppmvd @ 15% O2 | lb/hr | lb/MMBtu -HHV |
| Sulfur Dioxide (SO2) | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| Nitrogen Oxides (NOx) | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| Particulate Matter (PM10) | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| Carbon Monoxide (CO) | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| Volatile Organics (VOC as CH4) | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |

#### Basis for Emissions Data:

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

PM values are per US EPA Method 5/202 (front and back half).

Based on Siemens F4 Ultra Low NOx Combustor.

(SO2 lb/hr taken from performance that assumes a barometric pressure of 14.276).

Values are per stack and reflect the following conditions:

- 95°F ambient temperature.

  - CT at REDACTED% load.

  - Evaporative Cooler running (effectiveness REDACTED%).

  - 14.276 psia ambient pressure (gas), 14.59 psia ambient pressure (oil).

- Sulfur content in Oil is assumed to be REDACTED% (Ultra Low Sulfur Diesel).

- Lb/MMBtu values reflect REDACTED MMBtu/hr - HHV  of natural gas for natural gas emissions and REDACTED MMBtu/hr – HHV of Ultra Low Sulfur Diesel for oil cases.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### DEMAND EQUIVALENT FORCED OUTAGE RATE - EFORd (%) (The probability that the unit will not produce power when demanded.) | REDACTED |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | GAS Output = REDACTED% Heat rate = REDACTED% OIL Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED for a 350 MW site and REDACTED for a 700 MW site |

## TECHNOLOGY FORECAST

PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present to 2015 | 2015+ |
| --- | --- | --- |
| Representative Technology: | Siemens F4 | F Class (Enhanced) |
| Peaking Heat Rate (based on HHV ) | REDACTED | REDACTED |

Performance estimates based on the current trends as well as the anticipated equipment demand and technological enhancements.

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| F-Class (Dual Fuel) Two Unit |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |  |
| 1 | REDACTED | REDACTED |  |
| 2 | REDACTED | REDACTED |  |
| 3 | REDACTED | REDACTED |  |
| 4 | REDACTED | REDACTED |  |
| 5 | REDACTED | REDACTED |  |
| 6 | REDACTED | REDACTED |  |
| 7 | REDACTED | REDACTED |  |
| 8 | REDACTED | REDACTED |  |
| 9 | REDACTED | REDACTED |  |
| 10 | REDACTED | REDACTED |  |
| 11 | REDACTED | REDACTED |  |
| 12 | REDACTED | REDACTED |  |
| 13 | REDACTED | REDACTED |  |
| 14 | REDACTED | REDACTED |  |
| 15 | REDACTED | REDACTED |  |
| 16 | REDACTED | REDACTED |  |
| 17 | REDACTED | REDACTED |  |
| 18 | REDACTED | REDACTED |  |
| 19 | REDACTED | REDACTED |  |
| 20 | REDACTED | REDACTED |  |
| 21 | REDACTED | REDACTED |  |
| 22 | REDACTED | REDACTED |  |
| 23 | REDACTED | REDACTED |  |
| 24 | REDACTED | REDACTED |  |
| 25 | REDACTED | REDACTED |  |
| 26 | REDACTED | REDACTED |  |
| 27 | REDACTED | REDACTED |  |
| 28 | REDACTED | REDACTED |  |
| 29 | REDACTED | REDACTED |  |
| 30 | REDACTED | REDACTED |  |
| 31 | REDACTED | REDACTED |  |
| 32 | REDACTED | REDACTED |  |
| 33 | REDACTED | REDACTED |  |
| 34 | REDACTED | REDACTED |  |
| 35 | REDACTED | REDACTED |  |
| 36 | REDACTED | REDACTED |  |
| 37 | REDACTED | REDACTED |  |
| 38 | REDACTED | REDACTED |  |
| 39 | REDACTED | REDACTED |  |
| 40 | REDACTED | REDACTED |  |
| 41 | REDACTED | REDACTED |  |
| 42 | REDACTED | REDACTED |  |
| 43 | REDACTED | REDACTED |  |
| 44 | REDACTED | REDACTED |  |
| 45 | REDACTED | REDACTED |  |
| 46 | REDACTED | REDACTED |  |
| 47 | REDACTED | REDACTED |  |
| 48 | REDACTED | REDACTED |  |
| 49 | REDACTED | REDACTED |  |
| 50 | REDACTED | REDACTED |  |

| F-Class (Dual Fuel) Four Unit |  |  |
| --- | --- | --- |
| Month | Monthly % | Cumulative |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |

## INDICATIVE PROJECT SCHEDULE

REDACTED

## INDICATIVE PROJECT SCHEDULE

REDACTED

# RENEWABLE TECHNOLOGIES

The cost and performance data included in this section represent screening level estimates intended for general planning analyses.  As with any generation technology, detailed project-specific analysis may indicate cost and performance data materially different from the screening-level information due to site-specific conditions, regulatory considerations and market dynamics.  Nothing in this section should be interpreted as an endorsement or commitment on the part of Southern Company with regard to any renewable technology alternative.

PEAK LOAD INCREMENTAL HYDRO

NOMINAL 5 MW UPGRADE

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### Incremental Hydro refers to the incremental energy and in some cases, incremental capacity obtained by adding generating facilities or upgrading the existing facilities at existing impoundments. Upgrades to existing facilities are usually site specific and could range from replacing worn out equipment (such as a turbine runner) to replacing the entire powerhouse.  The addition of a generating facility is most commonly implemented by installing a new powerhouse in an underutilized impoundment.

###### Incremental Hydro could be achieved by several means and it is                                 crucial to weigh the site-specific regulatory, licensing, and environmental issues against the potential energy benefits, before selecting the appropriate upgrade(s) to pursue. Some of the common ways to generate incremental hydro are listed below.

###### Improving Efficiency

###### This is typically accomplished by replacing the turbine runner (water wheel).  A new turbine runner will regain efficiency that has been lost over time due to wear and with a modern design; the efficiency is often several percent higher than the original runner at installation.  Runner replacement and other hydraulic improvements to the turbines can increase energy production by REDACTED percent.

###### Upgrading Existing Capacity

###### Capacity increases typically require the replacement of the runner and significant upgrades to the generator and other electrical components to operate at higher power levels.  Incremental generation comes from both increases in efficiency and the ability to use more water.  With the higher capacity, water that would have been previously spilled will be utilized to generate energy.  Capacity increases at existing units generally range REDACTED percent.  The resulting incremental energy is dependent on the efficiency increase and the amount of spill that can then be used for generation.

###### Replacing Existing Unit

###### In some cases, it is more economical to replace older, low capacity, and inefficient generating units with newer units which results in considerably higher energy production.  In this case incremental energy results from both efficiency increase and reduction of spill.

###### Optimizing Minimum Flow Releases

###### Several existing hydro facilities have strict requirements to maintain minimum flows for environmental and recreational reasons.  The release rates are often such that the existing turbines cannot operate efficiently at that level.  Energy can be generated from minimum flow releases through modifications to existing turbines or by the adding a dedicated unit designed to operate at the required release rates.

###### Adding New Capacity

###### The addition of generating facilities at an existing underutilized impoundment can also be considered as Incremental Hydro.  There are a number of Corps of Engineer Locks and Dams that are not electricity generation facilities. Additionally, some of the existing hydro facilities have sufficient infrastructure to accommodate additional generator and turbine.  Adding new capacity at existing underutilized impounds offers the most energy and capacity benefits of all the Incremental Hydro upgrade opportunities.

###### Hydrokinetic Turbines

###### These are an emerging and largely unproven technology to extract small amounts of energy from flowing water without the need for a dam.  Hydrokinetic Turbines can also be deployed downstream of existing hydro facilities.   Some of the potential advantages of Hydrokinetic Turbines include minimal impact on net head and water quality.

#### State of Technology

###### For the most part Incremental Hydro upgrades comprise of mature technologies that are currently available. However, certain technologies like Hydrokinetic Turbines remain unproven on a commercial scale.

### HEAT RATE AND OUTPUT DATA

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Annual Average | N/A | 5,000 |

#### Basis for Heat Rate and Output Data:

Generic Peak Capacity assumed to have REDACTED% Capacity Factor.

### TOTAL PLANT COSTS

#### Note: Plant costs depend on the type of upgrade pursued. Cost for a Nominal 5 MW Equivalent Facility Upgrade is provided

|  | Per Kilowatt | Total |
| --- | --- | --- |
| Turnkey EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on 5,000 kW net output.

Existing hydro site.

All Site Costs assumed to be included in Turnkey EPC contract.

Interconnection Costs not included.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/13 and are for a plant completion date in 2016.

### O & M COSTS

#### Nominal 5 MW Equivalent Facility:

#### Fixed O&M Costs

###### (Based on 5,000 kW Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on 5,000 kW Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Major Maintenance Costs

###### (Based on 5,000 kW Rating and a REDACTED% Capacity Factor)

| Mills/kWh | - |
| --- | --- |
| Total/Yr | - |

### EMISSIONS

|  | Lbs/MMBtu |
| --- | --- |
| Sulfur Dioxide (SO2) | - |
| Nitrogen Oxides (NOx) | - |
| Particulate Matter (PM) | - |
| Carbon Monoxide (CO) | - |
| Carbon Dioxide (CO2) | - |
| Volatile Organics (VOC) | - |
| Mercury (Hg) | - |

#### Basis for Emissions Data:

Hydro facilities have no air emissions.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT FORCED OUTAGE RATE (Includes forced outages, maintenance outages and deratings) | N/A |
| ### EXPENDITURE DATA ATTACHED? | No |
| ### PROJECT SCHEDULE ATTACHED? | No |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) | REDACTED |

# BASE LOAD LANDFILL GAS TO ENERGY NOMINAL 3.2 MW

## PLANT DESCRIPTION AND DATA SUMMARY

### GENERAL DESCRIPTION OF THE PLANT

###### The landfill-gas-to-energy (LFGTE) facility is based on two Caterpillar G3520C reciprocating engines with an approximate electrical power output of 1,600 kilowatts each. These engine-generator sets combust landfill gas (predominately methane) produced from the natural anaerobic decomposition of municipal solid waste in a sanitary landfill. LFGTE facilities are easily scaled to match the gas production of a given landfill site by simply adding incremental engines to the plant.  Small landfills producing only enough gas sufficient to operate one engine are typically developed with containerized designs in which a single engine-generator set and auxiliary equipment is housed in a pad-mounted container.  For 2-Engine plant designs and larger, standard practice calls for the construction of a brick and mortar facility that houses the majority of equipment and includes a plant control room.

###### Plant cost basis and features for the 2-Engine facility include:

- Two CAT 3520C-LE Engine-Generator Sets (3.2 MW Gross Output)

- Fuel Gas Compressor

- Switchgear and Motor-Control Center

- Pad-mounted Generator Step-Up Transformer

- Architectural Block Building

###### Assumptions:

  - Landfill gas collection facility will be installed and/or operated by landfill entity to deliver landfill gas to plant boundary.

  - Energy produced at facility can be delivered onto the electric distribution or transmission system at a reasonably close interconnection point.

#### State of Technology:

###### This is a mature technology and currently available.

### HEAT RATE AND OUTPUT DATA

#### 2-CAT 3520C Reciprocating Engine Facility:

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Annual Average | REDACTED | REDACTED |

#### Basis for Heat Rate and Output Data:

Performance is net to the high side of the GSU and includes 165 kW of station service.

Heat Rate assumes quality of landfill gas at REDACTED% methane content equating to a lower heating value of approximately REDACTED mmbtu/ft3.

### TOTAL PLANT COSTS

#### 2-CAT 3520C Reciprocating Engine Facility:

|  | Per Kilowatt | Total |
| --- | --- | --- |
| Turnkey EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner’s | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on REDACTED kW net output.

Generic site located on or adjacent to landfill (assumed to be leased from landfill for a minimal amount).

All Site Costs assumed to be included in Turnkey EPC contract.

Interconnection Costs not included.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 3/1/11.

### O & M COSTS

#### 2-CAT 3520C Reciprocating Engine Facility:

#### Fixed O&M Costs

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

###### (Based on REDACTED kW Rating).

###### Costs are overnight as of 1/1/12.

#### Variable O&M Costs

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

###### (Based on REDACTED kW Rating and a REDACTED% Capacity Factor).

###### Costs are overnight as of 1/1/12.

### EMISSIONS

|  | 2-Recip. Engines Lbs/MMBtu |
| --- | --- |
| Sulfur Dioxide (SO2) | REDACTED |
| Nitrogen Oxides (NOx) | REDACTED |
| Particulate Matter (PM) | REDACTED |
| Carbon Monoxide (CO) | REDACTED |
| Carbon Dioxide (CO2) | REDACTED |
| Volatile Organics (VOC) | REDACTED |
| Mercury (Hg) | REDACTED |

#### Basis for Emissions Data:

CAT 3520C emissions based on 2 engine steady state operating conditions assuming a fuel lower heating value (LHV) of REDACTED Btu/ft3.

These emission estimates should only be used to generally characterize emissions.  Permits obtained in the future for this technology may require more stringent emission limitations than those estimates shown above.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT FORCED OUTAGE RATE (Includes forced outages, maintenance outages and deratings) | N/A |
| ### EXPENDITURE DATA ATTACHED? | Yes |
| ### PROJECT SCHEDULE ATTACHED? | Yes |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% Heat rate = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) | REDACTED |

## TecHnology discussion

Landfill-Gas-to-Energy Technology

With the uncertainty surrounding potential climate legislation and the increasing desire for sustainable “green” technologies, landfill-gas-to-energy projects have been on the rise as a viable source of renewable generation.  As landfills collect and dispose of waste, the natural decomposition of the organic material produces methane and carbon dioxide. If uncontrolled, landfill gas escaping into the air can contribute to smog, create an unpleasant odor, and present other safety and health hazards. Additionally, according to the EPA, methane has more than 20 times more impact than CO2 as a greenhouse gas.  As landfills produce nearly 23% of human-made methane, the EPA has set regulations under the Clean Air Act requiring landfills, which meet particular size and emissions thresholds, to collect and destroy the landfill gas.  These requirements typically come out of the New Source Performance Standards (NSPS) of the Clean Air Act, and landfills which fall under NSPS must follow specified procedures for installing a gas collection system, destroying the landfill gas, and submitting the appropriate reports to demonstrate compliance.  Once a collection system is in place, the gas destruction is often accomplished by simply flaring the gas, but alternatives have been developed to utilize the energy content of the methane for beneficial purposes.  The three primary options for the gas are as follows: electricity generation, direct use as a commercial fuel (industrial boilers, cement kilns, etc.), or refinement to pipeline-quality natural gas.  For the purposes of this discussion, the focus will be on the use of landfill gas for electricity generation.

In order to collect the gas from a landfill (whether voluntary or required by NSPS), the landfill will install collection wells into the various cells where the waste has been compacted for decomposition.  These wells are then connected by headers which feed into a blower that keeps the wellfield under a vacuum to draw the gas from the ground into the wells and ultimately to the flare or other end use.  Prior to utilizing the gas in an electric generator, condensate and particulates will be removed from the gas stream, and depending on the particular application and gas quality additional pretreatment may be required (to eliminate contaminants such as H2S and siloxanes).  Figure 1 below depicts a basic configuration for a landfill-gas-to-energy facility located adjacent to a landfill.

Figure 1: Typical Landfill-Gas-to-Energy Facility1

There are three principal electric generating technologies for landfill gas applications.  The first technology, and by far the most popular, is the internal combustion engine (reciprocating engine).  These engines, usually between 800 kW and 3 MW, are built to combust the low-BTU landfill gas and can often handle greater amounts of impurities in the fuel without requiring pretreatment.  Because of their rugged design, low capital cost and low O&M costs relative to the other technologies, reciprocating engines tend to be quite attractive.  The two manufacturers of reciprocating engines which have the largest presence in the U.S. are Caterpillar and Jenbacher (subsidiary of GE Energy).  Gas turbines are the second landfill gas technology, and these are usually seen for projects 3 MW and larger.  Gas turbines may provide better emissions characteristics than do the reciprocating engines, but higher capital costs often put the turbines out of reach.  The principal seller of small gas turbines capable of burning landfill gas is Solar, which is a Caterpillar-owned company.  The final technology represented in the landfill gas industry is microturbines.  There have been many successful microturbine installations using landfill gas at commercial or industrial facilities, but as these are only 30 kW to 250 kW in size, it is usually not economic for a utility interconnect application.  Figure 2 depicts a comparison of the number of projects with each generating technology for landfill gas.

Figure 2: Landfill Gas Technology Utilization1

1Landfill Methane Outreach Program (LMOP). U.S. Environmental Protection Agency.

<http://www.epa.gov/lmop/>.

## EXPENDITURE DATA

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

| Reciprocating Engine Spending Curve (2 Engines – 3.2 MW) |  |  |
| --- | --- | --- |
| Month | Monthly Payment Percent of Contract Price (%) | Cumulative Percent of Contract Price (%) |
| Month 1 | REDACTED | REDACTED |
| Month 2 | REDACTED | REDACTED |
| Month 3 | REDACTED | REDACTED |
| Month 4 | REDACTED | REDACTED |
| Month 5 | REDACTED | REDACTED |
| Month 6 | REDACTED | REDACTED |
| Month 7 | REDACTED | REDACTED |
| Month 8 | REDACTED | REDACTED |
| Month 9 | REDACTED | REDACTED |
| Month 10 | REDACTED | REDACTED |
| Month 11 | REDACTED | REDACTED |
| Month 12 | REDACTED | REDACTED |
| Month 13 | REDACTED | REDACTED |
| Month 14 | REDACTED | REDACTED |
| Month 15 | REDACTED | REDACTED |
| Month 16 | REDACTED | REDACTED |

## PROJECT SCHEDULE (Indicative only)

# GRID-CONNECTED SOLAR PHOTOVOLTAICS (PV) – UTILITY SCALE

## General Description

### Description

In general, a solar photovoltaic (PV) cell captures sunlight and converts it into DC electrical power.  The PV cells are put together in a module.  The number of cells contained per module depends on the manufacturer.  The modules are put together in an array, and the arrays are strung together and hooked to an inverter, which converts the DC power into AC power.  The AC power is stepped up, if necessary, with a transformer and the power is placed on the grid.

The amount of production from solar PV depends on the solar resource in the region.    The National Renewable Energy Lab (NREL) has several data sets available to allow for an estimation of the region’s solar resources.  From these values, the production from a solar PV system can be estimated.

NREL has also developed a model, Solar Advisor Model (SAM) https://www.nrel.gov/analysis/sam/ , that allows the user to input specific parameters and be able to design a solar PV plant.

### State of the technology

There are several types of solar PV cells:  crystalline, thin-film, heterointrinsic junction (HIT) and concentrated.  They differ in material, manufacturing process, and efficiency or, in other words, the amount and range of solar radiation they capture.  In general, the efficiencies are lower for thin film cells and higher for crystalline cells, but the costs are higher for crystalline than thin film.  Also, thin film manufacturers tout that their cell’s performance is not as dependent on temperature as crystalline’s.  The concentrated PV cells work better for direct sunlight. (Sunlight is described as being two types: direct and diffuse.  Direct sunlight is the sunlight that comes straight from the sun and diffuse sunlight is the sunlight that goes through clouds, reflects off of surfaces, etc.  The Southeastern U.S. has more diffuse sunlight than the Southwest U.S., which has more direct sunlight.)

The equipment is modular; thus, the size of the PV system depends on the number of modules strung together and combined with other strings.  The required equipment for a PV system is the modules, the inverters, combiner boxes, wiring, racking, and mounting equipment.

The goal is to obtain the most sunlight as possible, so as to achieve the best power production for the system.  Several ways to maximize energy production are to orient the modules due “true” south, use racking for mounting the modules at an angle equivalent to the system’s latitude, make sure no shading of the modules occurs, and use tracking that allow the modules to follow the sun’s path.

### Potential advancement of the technology

There currently is a significant amount of research work being done to improve the performance of this technology and lower its cost.  Also, a significant amount of work is being done on energy storage.  Once energy storage becomes more economic and usable, the issues with solar PV will be alleviated.  For example, energy storage will allow the peak operation of solar PV to be shifted to the times when a utility’s peak demands occur.

## Performance and Cost

### Size

* Amount of Generation  Note: The solar industry reports everything in DC rather than AC.

* Area Needed  The amount of area needed is dependent on type of solar PV cell used because the efficiency of the different technologies varies.  For example, thin film PV systems have lower efficiencies than crystalline PV systems and thus require more land per MW.

* Area needed per MW:  5-10 acres per MW

From Energy Insights, August 2009

This figure can be used to compare two competing solar technologies and determine the price of land at which savings due to lower system install costs for one technology are offset by savings from more efficient land use by a competing technology.

The land price at which the cost differences offset each other is represented on the y-axis; the x-axis represents the difference in total system install costs between two competing technologies.

Total system install costs include the costs of solar modules plus the balance of system (equipment and engineering) costs, but do not include land costs.

### HEAT RATE AND OUTPUT DATA

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output MWAC |
| --- | --- | --- |
| Peak Output | N/A | 10 |

#### Basis for Heat Rate and Output Data:

Generic Peak Capacity assumed to have REDACTED% Capacity Factor.  It depends on solar insolation values at the specific location and the technology selected.

### TOTAL PLANT COSTS1

#### Note: Plant costs depend on the type of solar photovoltaic technology pursued. Cost for a Nominal 10 MWAC One-Axis Tracking Crystalline Silicon Flat-Plate Solar Photovoltaic Facility is provided

|  | Per KilowattAC | Total |
| --- | --- | --- |
| Turnkey EPC | - REDACTED | - REDACTED |
| Site | - REDACTED | - REDACTED |
| Owner's | - REDACTED | - REDACTED |
| Total Cost | - REDACTED | - REDACTED |

#### 1. Source: Publicly Available Data/Vendor Quote.

#### Basis for Plant Costs:

All Site Costs assumed to be included in Turnkey EPC contract.

Interconnection Costs not included.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12 and are for a plant completion date in 2012.  EPC for a 10 MW plant can be completed in one year.

### O & M COSTS

#### Nominal 10 MWAC Equivalent Facility:

#### Fixed O&M Costs

###### (Based on 10 MWAC Rating)

| $/kW-Yr | - REDACTED |
| --- | --- |
| Total/Yr | - REDACTED |

#### Variable O&M Costs

###### (Based on 10 MWAC Rating and a REDACTED% Capacity Factor)

| Mills/kWh | - |
| --- | --- |
| Total/Yr | - |

#### Major Maintenance Costs

###### (Based on 10 MWAC Rating and a REDACTED% Capacity Factor)

| Mills/kWh | - |
| --- | --- |
| Total/Yr | - |

### EMISSIONS

|  | Lbs/MMBtu |
| --- | --- |
| Sulfur Dioxide (SO2) | - |
| Nitrogen Oxides (NOx) | - |
| Particulate Matter (PM) | - |
| Carbon Monoxide (CO) | - |
| Carbon Dioxide (CO2) | - |
| Volatile Organics (VOC) | - |
| Mercury (Hg) | - |

#### Basis for Emissions Data:

Solar facilities have no air emissions.

| ### PLANT LIFE (yrs) | - REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | - REDACTED |
| ### EQUIVALENT FORCED OUTAGE RATE (Includes forced outages, maintenance outages and deratings) | - N/A |
| ### EXPENDITURE DATA ATTACHED? | No |
| ### PROJECT SCHEDULE ATTACHED? | No |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) | REDACTED |

# WIND POWER GENERATION - UTILITY SCALE

## Description

### General Description

In general, a wind turbine converts the kinetic energy from the wind into mechanical energy and then turns it into electrical energy.  There are several different ways of achieving this, but in general, the turbine blades turn in the wind and respectively turn a shaft which turns the gears which turn the generator creating electricity.

The amount of production from a wind farm depends on the wind resource in the region.  The National Renewable Energy Lab (NREL) has data available to allow for an estimation of the region’s wind resources.  However, the best method of estimating the production from a wind farm is to strategically position meteorological towers fitted with anemometers at different heights and to record wind data for a minimum of one year.  Using this data, the production from a wind farm can be estimated.

The wind resource in the Southeast U.S. is very limited.  There are areas located in the Georgia and Alabama mountains that might have enough wind resource for potential wind generation.  However, the environmental issues, such as with bats and the “Not in my backyard” issues may prevent any exploration of taking advantage of this possible resource.  Another possible location is offshore.  A feasibility study was conducted by Southern Company and Georgia Tech looking at the potential wind resource off the coast of Georgia and a final report was prepared.   A copy of this report can be obtained by contacting SCS Research & Environmental Affairs (see end of document for contact information).

In general, this work found that more research needed to be done to better examine the potential wind resource off the Georgia coast.  This would be accomplished by the strategic placement of meteorological towers.  Once the wind resource is defined and a technology is built that can withstand the marine hazards and hurricane force winds, then this might provide an option for wind power generation.

### State of the technology

Wind power generation has seen significant recent growth.  The American Wind Energy Association (AWEA) reports through the end of the first half of 2012, 49,802 MW of wind power generation have been installed.  Another 10,300 MW are under construction.  Texas is the leading state with 10,648 MW installed.

The main issue with wind generation is that it is intermittent and land-based wind farms experience their peak generation at night which is when utilities are seeing their smallest demand.

### Potential advancement of the technology

The goal is to capture as much of the wind as possible, to best utilize the wind resource that is available, and to be able to survive environmental conditions such as lightning strikes.  Different turbine equipment designs, turbine blades, etc. are being developed to accomplish these goals.  Currently there are only a few turbines that are touted to withstand wind speeds that are experienced during Class 3 or higher hurricanes.  These turbines are designed to withstand these wind speeds but at a loss of efficiency.

## Performance and Cost

### Size

* Area Needed: The amount of area needed is dependent on size of the wind turbine.  The efficiencies improve if the wind patterns around a wind turbine have the chance to reestablish before they experience the next wind turbine.

* Area needed per MW:  While the area and impacts associated with physical infrastructure such as the wind turbines themselves may be the easiest to quantify, the more commonly cited land-use metric associated with wind power plants is the footprint of the project as a whole. However, unlike the area occupied by roads and pads, the total area is more challenging to define and subjective in nature. Generally, the total area of a wind power plant consists of the area within a perimeter surrounding all of the turbines in the project. However, the perimeter is highly dependent on terrain, turbine size, current land use, and other considerations such as setback regulations.  There is typically no uniform definition of the perimeter or boundary surrounding a wind power plant – in fact, the total area of a wind power plant could have a number of definitions.  The boundary could be defined based on the required turbine spacing as a function of rotor diameter, or use a standardized setback from turbines at the edge of a project.   Based on NREL data, land requirements for wind farms can range from 30 acres/MW to 140 acres/MW, depending on site-specific conditions.

Source:

Land-Use Requirements of Modern Wind Power Plants in the United States

Technical Report NREL/TP-6A2-45834, August 2009

### HEAT RATE AND OUTPUT DATA

|  | Net Plant Heat Rate (Based on HHV) Btu/kWh | Net Unit Output kW |
| --- | --- | --- |
| Annual Average | N/A | 20,000 |

#### Basis for Heat Rate and Output Data:

Generic Peak Capacity assumed to have REDACTED% Capacity Factor (CF).  It depends on the wind resource and the amount of wind turbulence.  For example, wind farm installations on ridge tops see a REDACTED% CF while the wind farms installed on the flatlands in Texas see up to REDACTED% CF.  These CF values are improving with technology improvements.

### TOTAL PLANT COSTS1

#### Note: Plant costs depend on the type of wind technology pursued. Cost for a Nominal 50 MW Facility is provided

|  | Per Kilowatt | Total |
| --- | --- | --- |
| Turnkey EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### 1. Source: 2011 Wind Technologies Market Report, Wiser R. and M. Bolnger. LBNL-5559E. August 2012.

#### Basis for Plant Costs:

All Site Costs assumed to be included in Turnkey EPC contract.

Interconnection Costs not included.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/11 and are for a plant completion date in 2012.  Construction for a 50 MW plant can be completed within REDACTED.  The issue with wind farms is the length of time required for permitting and for interconnection of these facilities.

### O & M COSTS1

#### Nominal 50 MW Facility:

#### Fixed O&M Costs

###### (Based on 50,000 kW Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs

###### (Based on 50,000 kW Rating and a REDACTED% Capacity Factor)

| Mills/kWh | - |
| --- | --- |
| Total/Yr | - |

#### Major Maintenance Costs

###### (Based on 50,000 kW Rating and a REDACTED% Capacity Factor)

| Mills/kWh | - |
| --- | --- |
| Total/Yr | - |

#### 1. Source: Renewable Energy Technology Guide—RETG: April 2009 Update.   EPRI, Palo Alto, CA: 2009.1019300.

### EMISSIONS

|  | Lbs/MMBtu |
| --- | --- |
| Sulfur Dioxide (SO2) | - |
| Nitrogen Oxides (NOx) | - |
| Particulate Matter (PM) | - |
| Carbon Monoxide (CO) | - |
| Carbon Dioxide (CO2) | - |
| Volatile Organics (VOC) | - |
| Mercury (Hg) | - |

#### Basis for Emissions Data:

Wind farms have no air emissions.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT FORCED OUTAGE RATE (Includes forced outages, maintenance outages and deratings) | N/A |
| ### EXPENDITURE DATA ATTACHED? | No |
| ### PROJECT SCHEDULE ATTACHED? | No |
| ### EXPECTED PLANT DEGRADATION | Output = REDACTED% |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) | REDACTED |

# BASE LOAD BIOMASS FIRED

NOMINAL 50 MW

  - PLANT DESCRIPTION AND DATA SUMMARY

    - General Description of the Plant

The unit is based on a Jacobs study for a 50 MW non-reheat, biomass fired facility located at an existing coal fired electric generating plant.

Conceptual Design:

The plant is designed to operate at REDACTED% capacity factor.

The power generating facility is required to burn a woody biomass fuel blend capable of producing 50 MW net and utilizing a single bubbling fluidized bed (BFB) non-reheat boiler for steam generation. The boiler operates at 1,475 psig and 955° F at the boiler main steam stop valve. The corresponding turbine inlet steam conditions are 1,450 psig and 950° F. Plant cost basis and features include:

- Selective non-catalytic reduction (SNCR) system

- Single flow condensing steam turbine generator

- Air quality control systems (AQCS) including a selective non-catalytic reduction (SNCR) system, a dry sorbent injection system, and a baghouse.

- Material handling system for wood and ash and all associated appurtenances

- Four (4) stages of regenerative feedwater heating will be utilized

- Surface condenser

- Mechanical draft cooling tower

- Wood unloading facility

- Fly ash conveying and storage system

- Condensate storage and transfer system

- Closed cooling system

- Fire protection system

- Instrument compressed air system

- Plant drains

- Potable water distribution system

- Sanitary waste collection system

- Plant DCS

State of Technology

This is a mature technology and currently available.

    - Heat Rate and Output Data

Summary of Plant Performance

New and clean condition

| Case | REDACTED | REDACTED | REDACTED |
| --- | --- | --- | --- |
| Gross Plant Output kW | REDACTED | REDACTED | REDACTED |
| Plant Aux Power kW | REDACTED | REDACTED | REDACTED |
| Plant Aux Power percent | REDACTED | REDACTED | REDACTED |
| Net Plant Output kW | REDACTED | REDACTED | REDACTED |
| Boiler Efficiency, HHV percent | REDACTED | REDACTED | REDACTED |
| NPHR, HHV Btu/kWh | REDACTED | REDACTED | REDACTED |

Basis for Heat Rate Data and Output Data:

- Net plant performance is net to the high side of the GSU and includes station service.

- Expected Summer performance at 95°F dry bulb / 45% relative humidity / 77°F wet bulb.

- Expected Annual Average performance at 65°F dry bulb / 75% relative humidity.

Degraded condition

| Case | REDACTED | REDACTED | REDACTED |
| --- | --- | --- | --- |
| Gross Plant Output kW | REDACTED | REDACTED | REDACTED |
| Plant Aux Power kW | REDACTED | REDACTED | REDACTED |
| Plant Aux Power percent | REDACTED | REDACTED | REDACTED |
| Net Plant Output kW | REDACTED | REDACTED | REDACTED |
| Boiler Efficiency, HHV percent | REDACTED | REDACTED | REDACTED |
| NPHR, HHV Btu/kWh | REDACTED | REDACTED | REDACTED |

Basis for Heat Rate Data and Output Data:

- Net plant performance is net to the high side of the GSU and includes station service.

- Expected Summer performance at 95°F dry bulb / 45% relative humidity / 77°F wet bulb.

- Expected Annual Average performance at 65°F dry bulb / 75% relative humidity.

- Degradation of REDACTED% Output and REDACTED% Heat Rate.

    - Total Plant Costs

#### Nominal 50 MW Site (New and Clean):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Costs per kW are estimated at summer output, 50% moisture, without sootblowing.

An EPC/Turnkey project execution methodology is assumed. SCS will procure the long-lead equipment, such as the boiler, STG, fuel handling equipment, and the FGD/fabric filter and will assign these contracts to the EPC contractor. The EPC contractor will erect all equipment and provide the overall power plant performance guarantee.

#### Nominal 50 MW Site (Degraded):

|  | Per Kilowatt | Total |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner's | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

#### Basis for Plant Costs:

Per kW costs based on the peaking rating.

Generic “Greenfield” site.

Refer to scope definition and exclusions in the Introduction section of the IRP Generation Technology Data Book.

Plant costs are overnight costs as of 1/1/12.

Costs per kW are estimated at summer output, 50% moisture, without sootblowing.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

An EPC/Turnkey project execution methodology is assumed. SCS will procure the long-lead equipment, such as the boiler, STG, fuel handling equipment, and the FGD/fabric filter and will assign these contracts to the EPC contractor. The EPC contractor will erect all equipment and provide the overall power plant performance guarantee.

    - (NON-FUEL) O & M COSTS

##### Nominal 50 Mw site: Biomass

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

##### Nominal 50 Mw site: Biomass

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Degradation of REDACTED% Output and REDACTED% Heat Rate.
Emissions (New and Clean)

Emissions to atmosphere are estimated to be as follows:

| Particulate matter | REDACTED |
| --- | --- |
| Nitrogen oxides (NOx) | REDACTED |
| Sulfur dioxide (SO2) | REDACTED |
| Carbon monoxide (CO) | REDACTED |
| Volatile Organic Compounds (VOC) | REDACTED |

| - PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| - MAINTENANCE TIME (weeks/yr) | REDACTED |
| - EQUIVALENT FORCED OUTAGE RATE (Includes forced outages/de-ratings and maintenance outages/de-ratings) | Not Available |
| - EXPENDITURE DATA ATTACHED? | Yes |
| - PROJECT SCHEDULE ATTACHED? | Yes |
| - EXPECTED PLANT DEGRADATION | REDACTED% Output REDACTED% Heat Rate |
| - CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED |

## expenditure data

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

|  | 50 MW Biomass |  |
| --- | --- | --- |
| Month | 2013 IRP Expenditure Curve | 2013 IRP Expenditure Curve (Cumulative) |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |

## indicative project schedule

REDACTED

# APPENDIX

The cost and performance data included in this section represent screening level estimates intended for general planning analyses.  As with any generation technology, detailed project-specific analysis may indicate cost and performance data materially different from the screening-level information due to site-specific conditions, regulatory considerations and market dynamics.  Nothing in this section should be interpreted as an endorsement or commitment on the part of Southern Company with regard to any technology.

# CARBON CAPTURE WHITE PAPER, 2012

Background

The purpose of this paper is to provide basic information about CO2 emissions and sources of the emissions from fossil fuel-fired power generation plants.  It discusses existing and emerging technologies that could potentially be used to capture and remove CO2 from the flue gas streams of Pulverized Coal (PC) and Natural Gas Combined Cycle (NGCC) plants or the syngas streams from the Integrated Gasification Combined Cycle (IGCC) plants.  Following the discussion of CO2 capture, the transportation and sequestration of the captured CO2 will be discussed including the potential for long term storage in the underground geologic formations.  At the end, the economic impacts from CO2 capture, transportation and storage are presented.

## Source and Formation of CO2

In the U.S., 48% of the power is produced from coal and 22% from Natural Gas (NG), which account for 83% and 15% of the total CO2 emission in the power generation sector, respectively, as shown in Figure 1.

Figure 1.  US Primary Energy Sources and CO2 emissions in Power Generation Sector (EIA 2008)

Combustion of carbon-containing fossil fuels releases carbon dioxide (CO2), water (H2O) and heat.  The amount of CO2 formed is directly related to the carbon contents in the fuels. For every pound of carbon in the fuel that is combusted, 3.7 pound of CO2 is produced.

### Types of Fuels

There is a wide range of carbon and energy contents between NG and the various types of coal. The variation in NG (carbon content) is primarily caused by variations with impurity levels such as higher hydrocarbons and inert gases, and the variation is

relatively small in magnitude.  However, the variation in coal carbon content is significant and depends on the type and source of the coal as shown in Table 1. In order to determine the emission factors for each fuel type, average carbon and energy content for each fuel is used, assuming complete combustion of the carbon to CO2. Table 2 shows these emission factors reported by EPA analysis.

Table 1. Range of Carbon and BTU Contents in Various Fossil Fuels

|  | As Received Carbon Content (wt %) | Energy Content (Btu/lb HHV) |
| --- | --- | --- |
| Bituminous | 46-86 | 10,000-12,500 |
| Sub-bituminous | 35-45 | 8,300-12,500 |
| Lignite | 25-35 | 4,000-8,300 |

Table 2. Average Emission Factors Reported by EIA

|  | As Received Carbon Content (wt%) | Energy Content (Btu/lb HHV) | CO2 Emissions (lb/MMBtu) |
| --- | --- | --- | --- |
| Natural Gas | 75 | 1,027 Btu/CF | 117 |
| Bituminous | 67 | 11,945 | 205 |
| Sub- bituminous | 50 | 8,570 | 214 |
| Lignite | 37 | 6,435 | 216 |

### Note that the CO2 emissions per MMBTU for coal are roughly twice that of NG.

### Plant Operation

To calculate the emission factors based on the plant electricity output, the emission factors per fuel energy content is multiplied by the plant heat rate. Table 3 shows an example for a PC and NGCC plant.

Table 3. Example of CO2 Emission Factors Conversion based on Per Unit Electricity Output (MWh)

|  | - PC | - NGCC |
| --- | --- | --- |
| - Fuel Type | - Bituminous | - NG |
| - CO2 Emission (lb/MMBtu fuel energy content) | - 205 | - 117 |
| - Plant Heat Rate (Btu/kWhe) | - 9,750 | - 6,825 |
| - CO2 Emission (lb/MWhe output) | - 2000 | - 800 |

As seen from the above example, power plant efficiency greatly influences the CO2 emissions per unit of electricity output. High efficiency plants result in lower CO2 emissions. Figure 2 shows the plant efficiency impact to the CO2 emissions for coal fired and NG fired power plants.

Figure 2. Impact of Electrical Efficiency to CO2 Emission Factors

Increasing plant efficiency decreases CO2 emissions. However, large CO2 emission reductions will depend on capturing and storing CO2 in underground geologic formations.

CO2 Capture Technologies for Power Generation

Commercial processes to capture CO2 are utilized by various industrial applications to produce high purity gas streams for chemical manufacturing and food processing, as well as for sweetening of NG by removing hydrogen sulfide and carbon dioxide.

There are two primary configurations in capturing CO2 from power plants.  One is based on the post-combustion capture and the other is based on pre-combustion capture. Post-combustion capture involves removal of CO2 from the flue gas after the combustion process (after the boiler for PC plants or after combustion turbine for NGCC plants).  Pre-combustion removes CO2 from a gas stream (syngas) before it is combusted in the turbine, as the case for IGCC plants. This section will discuss various existing and emerging technologies for CO2 capture for these two primary capture configurations, as well as an alternative combustion concept, oxy-fuel combustion.

## Post-combustion CO2 capture

Post-combustion CO2 capture is applicable to both PC and NGCC plants.  The major difference is the CO2 concentration in the flue gas, which is about REDACTED vol% for a PC plant and around REDACTED vol% for a NGCC plant.  The lower the CO2 concentration is, the “harder” (higher energy requirement, larger reactors and higher cost per unit CO2) it is to capture the CO2.  Figure 3 shows the process flow diagram of a PC plant with CO2 capture.

Figure 3. Process Flow Diagram of a REDACTED MW PC Plant with CO2 Capture Technology

REDACTED

Capture of CO2 effectively and economically in a post-combustion configuration is challenging due to larger gas volume flow, lower CO2 concentrations, and presence of contaminants and other pollutants. The primary existing technology for CO2 removal from flue gas is solvent-based absorption. Other emerging post-combustion technologies include bio-fixation using algae, ion transport membranes and adsorption using carbonaceous solids. None of these last three have achieved the technology readiness level necessary for a commercial demonstration.

### Solvent-based Absorption

Removal of CO2 from the exhaust gas of a PC unit or NGCC using current commercial technologies utilizes chemical solvents.  The exhaust gas flows through an absorber column (similar to a scrubber) where the CO2 will dissolve into and react with the solvent.  The process produces a CO2-rich solvent stream and CO2-depleted exhaust gas stream. The CO2-rich solvent stream is then sent to the regenerator to break up the chemical bonds by boiling the solvent at a temperature of 210-280 oF.  The CO2 gas is released and the solvents are recovered for repeated cyclic use in the absorber.  Figure 4 shows a typical process flow diagram of a chemical absorption process.

Figure 4. Process Flow Diagram for Chemical Solvent Absorption System (MEA)

REDACTED

Alkanolamines-based solvents are the most readily available solvents for CO2 capture.   Monoethanolamine (MEA) is the most popular choice for this application due to its higher CO2 loading per gallon of solvent and its tolerance for oxygen. Unfortunately, the CO2-MEA bond is also the strongest among the various options, and requires the largest amount of energy (steam) to break the bonds apart during the regeneration process. The steam for the regeneration is usually extracted from steam cycle of the power plant, which consequently reduces the power output of the steam turbine.  There is an energy penalty associated with the station service required for the solvent circulation pumps and gas blowers (REDACTED kWh/tCO2).

In additional to the energy penalty, MEA solvents are also sensitive to the presence of various air pollutants and contaminants in the flue gas such as SOx, NOx, particulates, HCL, HF, mercury and other trace materials as well as O2. For example, SO2 and NO2 form heat stable salts with amine, which decreases the CO2 loading capacity. Therefore, reducing contaminants below acceptable levels is necessary and often becomes an economic trade-off between the costs of replenishing the solvent versus the cost of removing the contaminants in the gas pre-treatment process.

Several commercially available chemical solvents are listed in Table 4. The table also shows the maximum demonstrated capacity for CO2 capture.

Table 4. Commercial Amine Systems for CO2 Capture

| - Solvents | - Max Demo Capacities (tCO2/d) | - Comments |
| --- | --- | --- |
| - Kerr-McGee/ABB Lummus Crest Process | 800 | 15-20 wt% MEA to recover CO2 from coke and coal-fired boilers for soda ash and liquid CO2 preparations. |
| Fluor ECONAMINE | 320 | 30 wt% MEA with an inhibitor for corrosion resistance and specially tailored for O2-containing gas streams. |
| MHI KM-CDR | REDACTED | Proprietary sterically-hindered amines that was initially commercialized in a urea production application. Relative to MEA, it claims to have REDACTED; REDACTED; REDACTED; REDACTED, REDACTED due to REDACTED; REDACTED; REDACTED; and REDACTED. |

The two post-combustion CO2 capture technologies that Southern Company REDACTED for near-term deployment on existing or new combustion units at a commercial scale are Alstom’s Chilled Ammonia Process (CAP) and MHI’s KM-CDR process using KS-1 solvent. Southern Company is investigating and has invested in both of these technologies. REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED  REDACTED.

Southern Company Services co-funded (through EPRI) a REDACTED MW demonstration of the CAP technology at We Energies’ Pleasant Prairie Power Plant (P4). Accomplishments of the CAP demonstration included the integration of several unit operations into a complete process, high levels of CO2 removal (REDACTED%), a high purity CO2 stream, low ammonia emissions and regeneration at pressure. Energy use was as predicted at REDACTED% of gross heat input, which is a REDACTED% increase in heat rate. The pilot unit experienced several operational challenges that, unfortunately, were not overcome prior to the completion of the test campaign at P4.

Because none of the challenges experienced at P4 were considered insurmountable, the P4 pilot was followed by a REDACTED demonstration at AEP Mountaineer which began operation in September 2009. This demonstration was originally designed at a REDACTED MW scale but has experienced limitations to performance and capacity due to operation philosophy changes since the original design basis. As of 1/1/2010 the project had captured and released REDACTED tons of CO2 and injected over REDACTED tons into sequestration wells. The two on-site wells have exhibited lower permeability and porosity than expected. The CO2 capture efficiency is expected to increase to REDACTED% as the ammonia concentration increases and the project goal is to capture and geologically sequester REDACTED metric tonnes of CO2 per year.

Southern Company Services and MHI have completed the design and construction of a REDACTED MW pilot scale demonstration of the KM-CDR process at Barry 5. This plant will capture and sequester CO2 at a rate of REDACTED tons per day for two to three years beginning in 2011. Operation of the capture facility began on June 3, 2011. Integration with the pipeline and injection well is expected in the 3rd quarter of 2012.  Predictions include a parasitic power load of REDACTED% which corresponds to a REDACTED% increase in heat rate.

The costs for the REDACTED MW pilot can be scaled up to the company’s REDACTED MW reference plant using scale-up exponent of REDACTED from Perry’s Chemical Engineering Handbook. The result is a REDACTED% capital cost increase for a new coal fired plant with CCS, versus a new plant without CCS.

## Pre-combustion CO2 capture

Pre-combustion CO2 capture specifically targets IGCC processes where coal is oxidized (gasified) in the reduced environment of a gasifier to produce synthesis gas (syngas) that consists of primarily a mixture of H2 and CO. Syngas, after cooling and cleanup, is combusted in the turbine similar to that of a NGCC plant to produce power.

If CO2 capture is required, a water-gas-shift (WGS) reactor is added upstream of the acid gas recovery unit which utilizes water in the gas to convert the CO to CO2 and produce more H2. The CO2 is then separated from the syngas for further processing, while the high hydrogen syngas is sent to turbine.  If high CO2 removal is required, multiple WGS reactors in series are necessary. Figure 5 shows the process flow diagram of an IGCC process based on oxygen-blown gasifier with CO2 capture.

Figure 5. Process Flow Diagram for an IGCC with CO2 Capture

REDACTED

Unlike the low concentration and low pressure of the CO2 in the flue gas for PC and NGCC post-combustion capture, CO2 in the syngas is at high pressure (400-1000 psi) with higher CO2 concentrations (20-50%).  This results in smaller gas volume, smaller equipment, more efficient capture and therefore lower capital investment. In a typical IGCC process, sulfur is removed from gas stream as hydrogen sulfide (H2S) using the same chemical or physical solvents which are also effective for CO2 removal.  Therefore, when CO2 capture is required, an additional absorber is added to the H2S removal system.

### Solvent-based Absorption

Chemical solvents used for pre-combustion CO2 capture are similar to those described previously in the post-combustion process. Out of many amine-based solvents, MDEA is the preferred solvent choice for IGCC due to its higher CO2 loading, lower regeneration energy and low degradation from impurities.

In addition to chemical solvents, physical solvents are suitable when the gas is at higher pressure.  Many commercial solvents are available including Selexol, Rectisol, Fluor solvent and Purisol. Unlike the chemical solvents which bond with CO2, the CO2 is physically absorbed in the solvent according to Henry’s law (gas dissolved in solvents is directly proportional to the gas partial pressure) at high pressure and therefore, its binding energy is weaker than that of the chemical solvents. This leads to lower energy requirement for the regeneration process which is typically achieved by simply reducing the pressure through multiple stages.  In addition, physical solvents tend to be chemically inert to many chemicals in the syngas stream and hence there is less solvent degradation and corrosion to the equipment. This reduces the need for large quantities of makeup solvents. A typical Selexol process for IGCC process to remove both H2S and CO2 is shown in Figure 6.

Figure 6.  A Typical Process Flow Diagram for Selexol Solvent

REDACTED

In addition to chemical and physical solvents, hybrid solvents that combine the advantages of both types of solvents are also being developed such as Sulfinol and Sulfolane by Shell, aMDEA by BASF, UCARSOL by Dow and Flexsorb by ExxonMobil.

One major disadvantage for the above solvent-based systems in IGCC applications is the requirement to cool the gas stream below 100 oF upstream of the absorbers.  Once the H2S and CO2 are removed, the syngas is reheated before entering the combustion turbine.  This results in a significant loss in thermal efficiency.  New development in material and processes are aimed at warm gas processes that can accomplish CO2 removal at higher temperature to reduce the efficiency loss.

### Pressure/Temperature Swing Adsorption

Adsorption of CO2 with solids has been used in various industry applications such as purifying H2 in refinery process or NG sweetening process under high pressure.  The solid sorbents include activated carbon and molecular sieves.  Adsorption is typically carried out at elevated pressure while desorption is based on either pressure-driven, temperature-driven or combination of both. Three variations of the adsorption process are typically employed, including pressure-swing adsorption (PSA), temperature swing-adsorption (TSA) and pressure, temperature-swing adsorption (PTSA). The names are given based on the desorption methods.  For PSA, desorption is carried out simply by reducing the pressure in the regenerator.  For TSA, thermal energy is used to heat up the solid sorbents and drive off the CO2.  PTSA uses the heat to assist in the desorption process at reduced pressure. PSA by far is the most preferable method over the TSA which requires high thermal energy and longer cycle time to heat up the bed of solids. Figure 7 shows the flow diagram of the PSA.

Figure 7. Flow Diagram of the PSA Process

REDACTED

There are two major technical issues. One is that CO2 loading capacities in sorbents are greatly reduced over time if impurities are present in the gas stream. For example, water vapor could inhibit the CO2 adsorption onto sorbents such as alumina-silicates, zeolite and silica gel due to their high affinity to water and reduce their capacity for CO2 loading.  The other relates to a potentially large H2 loss through the adsorption process which would reduce the heating value of the syngas.

### Cryogenic Separation

Cryogenic separation is also a commercial process used for CO2 liquefaction or purification process. High CO2 concentration and high feed gas pressure is necessary to effectively employ this process. As result, cryogenic processes are more suitable for the pre-combustion IGCC processes than the post-combustion PC plant. The process is based on “distilling” the gas and occurs at very low temperatures. Separation or purification takes place as gases go through the condensation and evaporation processes at various

temperatures. Compression (to ~150 psi) and cooling are necessary to achieve the separation and thus increase capital cost and incur significant energy penalty. In general, cryogenic processes are less competitive than more traditional solvent-based system.

## Emerging Technologies

Emerging technologies address the major drawbacks of existing absorption processes, i.e. energy penalty for regeneration, parasitic loads and system complexity to different degrees. Though they hold the promise to make CO2 capture more economical and reliable in the long term, most of them are still in the early stage of the development process.

Advanced Solvents

Several advanced solvents are being explored to reduce the energy penalty and degradation to make CO2 capture more economical. Table 5 lists some of these solvents and their advantages for post-combustion CO2 capture. The energy penalty could potentially be reduced by REDACTED% and subsequently increase the thermal efficiency of the overall power plant.

Table 5. List of Advanced Solvent Systems

| - Advanced Solvents | - Benefits |
| --- | --- |
| - Ammonia-based Solvents (Alstom, Powerspan, NETL, etc.) based on the reaction of: - (NH4)2CO3 + CO2 + H2O ↔ 2 NH4HCO3 | - Low heat of absorption (REDACTED of MEA) - High CO2 loading capacity (REDACTED soln of MEA) - Low heating requirements for high pressure regeneration - Low cost (REDACTED of MEA) Stable reagent |
| - Amino Acid Salts (Siemens, BASF, DOW, TNO, etc) | - Potentially have high CO2 capacity, especially if solid phase is encouraged - Potentially reduce regeneration energy significantly (if solids are formed) - Low volatilities - High stability and resistance to degradation |
| Room Temperature Ionic Liquid (University of Notre Dame, ION Engineering, etc) | - Exceptional thermal, chemical and electrochemical stability. - Exhibit negligible vapor pressure - Can work at elevated temperature |

For pre-combustion CO2 capture process, several solvents mentioned above are also being explored such as ammonia chemistry and ionic liquids.  In addition, many companies are looking into the feasibility to utilize enzyme (e.g. Carbonic Anhydrase) to enhance the CO2 dissolution in water.

Solid Sorbents

In addition to the solvent-based absorption, researchers are also investigating dry, solid-based sorbent systems to scrub CO2 from syngas or flue gases. The approaches of developing solid sorbents for pre- and post-combustion capture processes are different. For post-combustion, since the flue gas is at low pressure, chemical modifications to the sorbent materials are often practiced to increase the CO2 loading.  In the syngas processes, high temperature sorbent materials could enable CO2 absorption at elevated temperature, which will reduce efficiency penalties from the capture process.  The potential advantages over the solvent-based systems include better contacting of the CO2-laden gas with the sorbent; smaller vessels; better temperature control; no need for massive quantity of water in the capture step; and less overall energy consumption.  In addition, the land area required for installation of the dry solid sorbent systems could be less than that of the wet scrubbing systems.

Membrane Technologies

A membrane serves as a selective barrier that allows some species to pass through the membrane while blocking others.  The feed gas containing all gas components enters on one side of the membrane.  The desired gas component permeates through the membrane and is collected at the opposite side of the membrane.  Membrane technologies for gas separation have been used in commercial processes such as NG sweetening, H2 recovery in the refinery process and ammonium production processes.  Since high differential pressures are typically required for gas membranes to function, this technology is more suited to IGCC at high CO2 partial pressure than PC or NGCC at low pressure. For PC, compressing the flue gas and/or lowering CO2 permeate stream (vacuum) are necessary to increase the driving force for CO2 permeation. For IGCC process, high temperature membrane process that separates H2 from CO2 (or vice versa) couples with an upstream warm gas cleanup process (e.g. RTI’s Warm Gas Desulfurization Process) could increase thermal efficiency significantly.

As an alternative approach, gas absorption membrane technology combines the membrane technology with the absorption solvents to remove CO2 from flue gas (hybrid membrane/absorption process).  These membranes act as the contacting devices between the gas and liquid phases without directly contributing to the CO2 selectivity and separation. Just as the traditional solvent systems, CO2 diffusing through the membranes is absorbed by the chemical solvents and stripped off the solvents in the regenerator.

## Oxy-Fuel Combustion

The concentration of CO2 in the flue gas is largely diluted by the N2 that is introduced with air into the PC boiler. Oxy-fuel combustion technology mitigates this problem by introducing nearly pure oxygen into the boiler instead of air. The resulting flue gas is comprised of primarily CO2 (50-65 vol%) and H2O vapor along with some N2, O2, and trace gases such as SO2, and NOx.  As a result, minimum CO2 separation and purification is required after water vapor is condensed. In this process, an air separation unit (ASU) is added to the processes to produce the nearly pure O2.  The combustion temperature is higher in the oxygen environment without N2 diluents, therefore to moderate this temperature increase, a portion of the flue gas is recycled back to the boiler.  Figure 8 shows a concept of the oxy-fuel combustion technology with flue gas recycling.

Figure 8. Concept of Oxy-combustion in PC Boilers with Flue Gas Recycling

REDACTED

CO2 Transportation, Utilization and Sequestration

After CO2 is captured and removed it has to be processed to proper conditions (pressure, temperature and compositions) for pipeline transportation and injection for underground sequestration (storage). The following section describes processes and requirements for CO2 transport, utilization, and storage.

## CO2 Compression

In order to deliver CO2 through pipeline for either underground storage or enhanced oil recovery (EOR), CO2 is typically compressed to supercritical conditions ( > 1,070 psi and  > 90 oF). A typical target pressure for CO2 transportation and injection is about 2200 psi to overcome the pressure exerted by underground formations, although injection pressures can vary significantly from one storage reservoir to another. Depending on the CO2 capture processes, multiple-stage compressors with intercoolers are required to achieve this pressure. The large compression energy requirement results in significant penalty to the plant output.

## CO2 Transportation

CO2 pipelines have been in commercial operations throughout the US with a total length exceeding 3,500 miles.  They transport about 50 MT/year of CO2 from natural sources to EOR projects in the west Texas and other areas. Figure 9 shows sources of the CO2 and existing pipelines in the U.S. In order to maintain the pipeline integrity, the CO2 gas stream has to meet a minimum quality requirement.  An example of such quality specification from Kinder Morgan’s pipeline in Texas is shown in Figure 10. As shown in the figure, it is crucial to keep concentration of O2 and H2O to a minimum to avoid corrosion problems around pipelines, valves and pumps. A dehydration unit is typically installed before the compression stage to ensure that the moisture level is at ppm level.

Figure 9. CO2 Sources and Existing Pipelines in US

REDACTED

Figure 10. Example of CO2 Specifications from Kinder Morgan’s Pipeline in TX

## CO2 Utilization

CO2 is currently injected into oil fields for enhance oil recovery (EOR). The injected CO2 allows operators to recover oil that would normally be left in the ground when a field reaches the end of its conventional production economic life. Most of the CO2 used for EOR comes from natural underground reservoirs, rather than being captured from combustion or industrial sources. EOR provides a near-term economic opportunity for CO2 capture from fossil power plants, especially in areas where oil fields or pipelines are located nearby.

Similar to EOR, CO2 can also be used to enhance the commercial recovery of coalbed methane (ECBM) from deep un-mineable coal seams, which accounts for about 6% of the total US NG production in 1998. Since CO2 adsorbs more easily onto the coal than methane, methane is displaced out of the coal and recovered while the reservoir pressure is maintained. There are limits in the application of ECBM to coal mines such as suitable geologic characteristics, moderate permeability, appropriate depth and minimum saturation levels.

In addition to the more traditional EOR and ECBM processes, many developers are exploring other CO2 uses such as algae growth for bio-fuel production and production of cement, methanol, polymers, etc.

## CO2 Storage

Once the CO2 is captured and transported to the storage site, it can be injected underground for long term storage. Although there is extensive experience of temporary gas storage in underground geologic formations and injection of CO2 for EOR, injection and long term storage of utility-scale CO2 volumes is not fully understood. Large storage demonstrations and field analyses are required to ensure that such storage operations can be accomplished safely and permanently without long term health and environmental impact.

There are several categories of potential underground formations for utility-scale long term storage consideration as shown in Figure 11. Among these choices, deep saline formations generally located between 3,000 and 10,000 feet below the sea level, have the greatest storage capacity. Most saline formations are composed of porous sandstones overlain by one or more impermeable rock formations (cap rock) such as shale or anhydrite and have the potential to seal storage formations and trap injected CO2.

Figure 11. Various Geologic Formations for Long-term CO2 Storage

REDACTED

In the U.S., the total CO2 storage capacity in various geologic settings, based on current estimates, is shown in Figure 12 based on the estimate from eight different regions.  To put these storage capacities in perspective, the total CO2 emissions from all sources in the U.S. is estimated to be about 3.8 billion tons per year. At this emission rate, the estimated storage capacity of CO2 is over several hundred years.

Figure 12. Capacity Estimates of CO2 Sources and Geologic Sequestration Sites

Storage formations must possess certain characteristics to be usable. They must contain proper permeability to accommodate the injection rate of the CO2 emissions from power plants. They also need to have integrity (e.g. no fault in cap rocks) to secure CO2 for a long time. In order to understand and characterize these formations, real world demonstrations are necessary. DOE has formed seven Regional Carbon Sequestration Partnerships to gain technical and operational insights of carbon storage by demonstrating carbon injection and storage in various geologic formations in different regions.  Another important aspect of these projects is to monitor the CO2 underground after the injection to determine the fate of the CO2, the interaction of the CO2 with underground minerals, and the diffusion and migration paths and its potential impact to surface ecosystems and resources. The knowledge collected through this program will assist in determining the feasibility and build confidence in geologic carbon storage as a means to reduce CO2 emissions from fossil fuel-fired power plants in the long term.

Figure 13. DOE Regional Carbon Sequestration Partnerships

Cost of CO2 Capture and Sequestration

Three major cost drivers for CO2 capture and sequestration include the cost of compression, cost of CO2 transportation and cost of sequestration. Among these three factors, CO2 capture cost, which is a function of CO2 partial pressure and concentration, represents about 80% of the total incremental cost. Table 6 summarizes some of the cost elements that contribute to the cost increase.

Table 6. Elements of Cost Increase Factors from CCS

| - Cost Increase Factors | - Contributing Elements |
| --- | --- |
| - Cost of capture | - New equipment (e.g. shift reactor, CO2 removal system, compression) - Existing equipment modification (larger coal feed & gas flow, gas pretreatment, larger ASU) - Parasitic loads (pumps, blowers, compressors) - Energy consumption (solvent regeneration) - Operation and maintenance cost (solvent replacement, reliability of components) |
| - Cost of Transportation (pipeline) | - Pipeline construction (materials, labor, booster station) - Operation (monitor and maintenance) - Special land conditions (population, national parks, crossing waterways, offshore, etc) - Others (design, insurance, right-of-way) |
| - Cost of Sequestration | - Proximity to host site - Reservoir depth - On or off-shore storage - Geologic characteristics (formation, permeability, thickness, etc.) - Monitoring, Verification, and Accounting |

DOE conducted a study and published a report “Cost and Performance Baseline for Fossil Energy Plants Estimate” in August 2007, which shows the impact of CO2 capture to cost and performance of various fossil energy power systems.  These results are summarized in Table 7.

Table 7. Summary of Impact of CO2 Capture to PC/IGCC/NGCC

|  | PCa | IGCCb | NGCC |
| --- | --- | --- | --- |
| Efficiency Reduction, % | 32% | 19% | 14% |
| Capital Increase, % | 85% | 36% | 112% |
| LCOE increase, % | 84% | 36% | 42% |

aAverage of subcritical and supercritical PC Plants

bAverage of GE, CoP and Shell Gasifiers (DOES NOT INCLUDE TRIG TECHNOLOGY)

Estimate of cost impact varies widely depending on the assumptions made for various capture processes, type of plants, plant life, fuel costs, site and plant specific characteristics (e.g. SOx, NOx, Hg controls in place), distance of CO2 transportation, location of sequestration sites and financial terms.  Table 8 reflects such variations and uncertainty from different studies. In the table, the cost of capture (in terms of LCOE) of the PC plants is the reference point. The costs of capture for other plants are presented relative to the reference plants. As shown, the LCOE increase ranges for IGCC without capture, PC with capture and IGCC with capture are 5-15%, 58-84% and 33-66%,

respectively, higher than the PC without capture. Therefore, it is critical to conduct specific site analysis in order to accurately project the total cost to capture and sequestrate the CO2.

Table 8. Comparison of Estimated LCOE Normalized to PC Plant without Capture

|  | No Capture |  | w/Capture |  |
| --- | --- | --- | --- | --- |
|  | PC | IGCC | PC | IGCC |
| MIT Study | 1 | 1.05 | 1.60 | 1.35 |
| GE Energy | 1 | 1.06 | 1.58 | 1.33 |
| AEP | 1 | 1.08 | 1.84 | 1.52 |
| GTC | 1 | 1.11 | 1.69 | 1.39 |
| DOE/NETL | 1 | 1.10 | 1.66 | 1.43 |
| EPRI | 1 | 1.15 | 1.58 | 1.66 |  |

Additional Considerations for CO2 Capture and Sequestration

In addition to overcoming technical hurdles and costs associated with capture, transport, and storage of carbon, other items must be satisfactorily addressed before such capture can become common place.

Land Use

The most promising means of storing carbon is geological sequestration, where CO2 is injected into underground storage formations.  Over time, as CO2 concentration builds, it disperses horizontally within the storage formation over a certain radius from the point source of injection.  Modeling indicates that long term injection from a single coal fired power plant may eventually cover a circular area of up to 10 miles in diameter (about 80 square miles).

Before full scale injection can occur, further work is needed to clarify land use particulars and rights of those involved, and to establish large and legal reservoirs.  Some questions that will need to be resolved, which could potentially make CO2 storage very expensive, are:

Does surface property over the projected radius of underground CO2 dispersion need to be acquired by the process owner in order to inject carbon into the underground formation?

Do existing land owners retain their land, lease it, reach an agreement with the process owner, or compromise their surface or mineral rights?

Who bears the cost of negotiating with landowners and with securing mineral rights?

Can or should eminent domain powers be utilized to obtain the property of others, or force them into negotiations?

These are unclear areas not addressed by law with regard to long-term CO2 storage; however, there is some precedent in the oil and gas industry as well as natural gas storage and hazardous waste injection.  The resolution of these issues remains to be seen and could have a significant effect on the viability of the technology.

Liability for CO2 Storage (and Transport)

When an underground formation has been selected that holds promise for sequestering CO2, attention then must be given to a survey of the area.  Penetrations (wells) into the storage area must be identified in the known area of CO2 storage.  Preexisting wells may have been drilled and abandoned.  Open wells may exist.  Some wells may have been capped (correctly or poorly), and other wells may simply escape efforts or technology in finding them.  Therefore, CO2 leakage pathways penetrating the storage formation should be identified then sealed.

In addition to identifying and sealing potential areas of CO2 escape, technology must be developed to monitor and verify that the CO2 remains in place, stored securely underground.  Monitoring techniques and mechanisms will also be required to verify storage permanence and validate CO2 reduction. Various above ground monitoring techniques (per region) are in research to figure out how to best verify secured storage and to identify and remedy leaks, should such occur.  In addition, if a leak does occur,

Who is responsible for it?

What liability is incurred and to whom, if a leak has harmful consequence?

Are financial instruments available for those who wish to purchase insurance to cover such liabilities?

In addition to the advancement of the technologies needed to verify secure storage, these significant questions must be answered as well.

CO2 Behavior

Once CO2 is injected into a saline formation (or into any resource for that matter) and continues to collect in the resource, it will interact with the reservoir as it begins to displace saline fluids already in the formation.  Further work is needed to understand behavior of the CO2 within the formation and the predictive ability to accurately model and map its dispersion over time.  Information will be gathered from two dozen validation phase geologic field tests being planned and in progress across the U.S. to gain a better understanding of the migration and interaction of liquefied CO2 as it accumulates in geologic formations.  Test are being conducted in saline formations, oil and gas bearing rocks, and in defunct coal seams.

Current and Planned CO2 Capture Projects

A list of existing and planned domestic and international CCS projects is listed in Table 9 and Table 10, respectively.

Table 9. Existing CCS Projects – Domestic and International (updated 6/7/2010))

| - Company | - Location | - Comment |
| --- | --- | --- |
| - Dakota Gasification Co. & EnCana & Apache Corp | - Beulah, ND and Weyburn, Canada and Midale, Canada | EOR, "industrial scale", multiple injection wells, 3 million tons a year from lignite coal, 40 million(gross) tonnes total |
| BP & Statoil | In Salah, Algeria | Onshore saline formation, 1 million tons a year from natural gas, one injection well |
| Statoil | Sleipner field, North Sea | Offshore saline formation, 1 million tons a year from natural gas, one injection well |
| ExxonMobil | LaBarge Plant, Wyoming | CFZ cryogenic separation process 4 million tons per year to be captured, used for EOR |
| Vattenfall | Schwarze Pumpe, Germany | 30 MW oxy-combustion system began operation in September 2008 |
| AEP | WV | 20 MW chilled ammonia capture demonstration; Project operated for approximately 18 months with ~60k tons captured and ~35k tons injected. |
| Southern Company | Mobile, AL | A 25 MW CO2 capture demonstration at Alabama Power’s Barry Plant using MHI KM-CDR process. 100,000 to 150,000 lbs of CO2 is captured annually for storage in a geological formation. |
| Southern Company | Wilsonville, AL | Southern Company manages and operates the DOE’s National Carbon Capture Center which will develop and test advanced technologies to capture carbon dioxide from coal-based power plants. |

Table 10. Planned CCS Projects – Domestic and International (6/7/2010)

| - Company | - Location | - Comment |
| --- | --- | --- |
| AEP | WV | 285 (electric) chilled ammonia capture demonstration, expected to capture 1.5 million metric tons of CO2 per year and use in EOR projects (– cancelled in July 2011) |
| Alberta Saline Aquifer Project (ASAP) Enbridge, Inc. | Alberta, Canada | 38 participants; Phase I complete, Phase II pilot project storage underway; 1.2 million tones per year from new EPCOR Genesee IGCC plant and post-combustion capture from a new 150 MW coal-fired plant beginning in 2015. |
| Ameren Energy | IL | Injection of 1 million tons CO2/year in IL Basin project (deep rock formations) |
| Ameren Energy | MO | Injection of 1 million tons CO2/year in shallow sandstone formation. |
| Babcock & Wilcox Air Liquide | OH | Ongoing 30 MW thermal pilot capture project on oxy-combustion. Recently completed test with bituminous coal and will also test PRB and lignite. Supporters include: AEP, AES, Basin Electric, EPRI, First Energy, Mid-American, SaskPower, PacifiCorp and others. |
| Basin Electric Power Coop | ND | Capture of 1 million tons CO2/year using HTC Purenergy capture technology; capturing 90% of a 120 MW slipstream for use in EOR – on hold indefinitely. |
| BP & Edison Mission Group | Carson, CA | pet coke to hydrogen and CCS, 500 MW, 4 mt CO2/commercial scale – formerly Hydrogen Energy now sold to another developer |
| Hydrogen Energy, JV of BP, Rio Tinto & Masdar | Abu Dhabi, UAE | natural gas to hydrogen and EOR CCS, 400 MW net, 1.7 million tones/year – ready in 2014? |
| DOE, USTAR, HCCS and others | UT | Injection of 1 million tons of CO2 into Farnham Dome saline formation |
| DTE Energy | MI | 250 tons of CO2/day in deep rock formations in the Michigan Basin for a total of 10,000 tons over 1 to 1.5 months; part of Midwest Regional Carbon Sequestration Partnership – status?(RAE) |
| Duke Energy, GE and Bechtel | Edwardsport Station, Knox County, IN | 630 MW IGCC plant under construction with operation scheduled in 2013. The addition of CCS is under consideration. Cost overruns have been filed for URC approval. |
| Quigg Energy LLC, Sunwest Management and Edison Mission Group | Gig Harbor, WA | Wallula Energy Resource Center - Plans to develop a 600 – 700 MW IGCC power plant which would burn Powder River Basin coal and store carbon dioxide emissions in underground basalt formations. No activity since 2008? |
| E.ON | Sweden | Post-combustion capture at Karlshamn power station using Alstom’s chilled ammonia process at capture rate of 30 tonnes/d |
| E.ON | Belgium | Partner with Hitachi Power Europe and Belgium’s Electrabel to build a test unit to test new, improved solvents. |
| E.ON |  | Plan to test Cansolv’s solvent technology. The modular unit will operate a flow rate of 20,000 m3 of flue gas per hour. |
| E.ON | Germany | Plan to test Siemens, Fluor and MHI solvent technologies at Staudinger, Wilhelmshaven coal-fired power plants – some of these on hold. |
| First Energy, BP & Powerspan | OH | PC and CCS, 1 MW pilot; storage in suitable rock formations such as saltwater reservoirs; part of Midwest Regional Carbon Sequestration Partnership; |
| FutureGen II | - | Upgrade a power plant in Meredosia, Ill. with oxy-combustion technology to capture approximately 1.3 million tones of CO2 per year. Ameren has pulled out as host due to retirement of asset. |
| GreenGen | Tianjin, China | Stage I: Build the 250 MW IGCC polygeneration plant. Stage II: Add CCS |
| NRG | Parish Plant, Sugar Land, TX | Post-combustion demo on flue gas equivalent to a 60 MW unit. Fluor’s Economine FG Plus amine based solvent and Ramgen CO2 compressor will be demonstrated. 90% CO2 capture will produce 500,000 tons per year to be used for EOR. To be operational in 2015. Project has been revised and scaled up to support large scale EOR (~250 MW) |
| RWE | Tilbury, UK | SC/PC and CCS, 1000 MW, commercial scale |
| RWE | Wales | Two post-combustion pilots - 1MW and a 25MW |
| Santos | Australia | Proposed a carbon storage project using the Moomba natural gas fields. If approved by the Australian government, this project would create the world's largest carbon dioxide storage facility. |
| SaskPower, Hitachi | Saskatchewan, Canada | Boundary Dam CCS Demonstration Project - 115 MW coal-fired power plant with Cansolv post-combustion amine scrubbing for 90% CO2 capture ; 1 million tonnes per year of CO2 will be sold for EOR purposes. Final decision to proceed late in 2010 for operation in 2013? |
| Mississippi Power Company | Kemper County, MS | A 582 MW IGCC plant designed for 65% CO2 capture is currently under construction. A final order from the Mississippi Public Service Commission was received on June 3, 2010. The project is 70% complete and commercial operation is scheduled to begin in May 2014. CO2 will be captured utilizing a Selexol system, a commercially available process that utilizes a physical solvent. The captured CO2 will be sold and sequestered through its use in enhanced oil recovery. |
| Total S.A. and Air Liquide | Lacq natural gas field, France | 30 MW Oxy-combustion process: 90% to 95% of CO2 will be captured and transported by pipe for storage in the depleted Rousse gas reservoir at a depth of 4500m. Projected 120,000 tonnes over two years |
| Vattenfall | Janschwalde, Germany | 385 MW CCS demonstration of oxyfuel and post-combustion capture of up to 2.7 million tones per year at a 90% capture rate—on hold |
| We Energies, EPRI and Alstom | Pleasant Prairie Power Plant, Kenosha, WI | 1.7 MW pilot capture with chilled ammonia process; testing started in 2008 and continued for about a year. |
| ZeroGen, Shell | Queensland, Australia | IGCC and CCS, 100 MW, 420,000 t CO2 annually |

More thorough list of CCS projects can be found at the following public domains:

IEA Greehouse Gas RD&D Database (http://www.ieaghg.org/index.php?/RDD-Database.html)

MIT CCS Project Database (http://sequestration.mit.edu/tools/projects/index.html)

# PULVERIZED COAL TECHNOLOGY DISCUSSION

Conventional Pulverized Coal Technology

With a backdrop of the presence of abundant, inexpensive coal, a need to keep up with growing base load capacity, and technological uncertainty surrounding CO2 capture and sequestration, it seems sensible to investigate higher efficiency Pulverized Coal as a resource planning option.  Newly constructed supercritical PC boilers are currently being designed to provide main steam and reheat steam at 1,050 0F or higher.  Advancements in metal alloys now allow main steam temperatures of 1,112 0F and reheat temperatures of 1,148 0F and pressures of 4,500 psia.  Many in the industry refer to these commercially available technologies that are “leading-edge” supercritical designs as “Advanced Supercritical”.  Ongoing research is pushing to aggressively extend the steam cycles.

There is a disconnect in the industry about the nomenclature of conventional supercritical steam cycles and the newer, higher pressures and temperatures.  One definition of Ultra-Supercritical is any main steam condition over 3,600 psia and approaching 1,100 0F is “Ultrasupercritical”.  Another definition of Ultra-Supercritical is over 3,600 psia and 1,100 0F or more.  Others refer to 1,100 0F main steam temperatures as “Advanced Supercritical”, which acknowledges the improvement in cycle efficiency and higher demands for metallurgy.  However, the material requirements were achieved without a step-change in metallurgy.  The next progression in metallurgy will be a step-change that is currently requiring intensive collaboration by dozens of industry participants.

Southern Company Engineering and Construction Services refers to what will be feasible with future advancements as “Ultra-Supercritical”.  Certain materials such as the development of high-nickel alloys could allow main steam temperatures to reach 1,292 0F and reheat temperatures to reach 1,328 0F.  However, these materials have not been fully developed or tested at this time.

To date, several Advanced Supercritical projects in the United States as well as projects worldwide have been completed or are soon to be completed.  The list of those projects is listed below.

Representative North American Supercritical PC Projects

| Power Plant Name (Owner) | Country | MW | Steam Pressure psia | Main Steam 0F | Reheat Steam 0F | Commercial Operation Date |
| --- | --- | --- | --- | --- | --- | --- |
| Walter Scott (MidAmerican) | USA | 790 | 3,690 | 1,050 | 1,100 | 2007 |
| Weston 4 (WPSC) | USA | 532 | 3,800 | 1,076 | 1,076 | 2008 |
| Comanche 3 (Xcel) | USA | 750 | 3,800 | 1,105 | 1,105 | 2010 |
| Iatan 2 (KCP&L) | USA | 850 | 3,686 | 1,085 | 1,085 | 2010 |
| Trimble County (LG&E) | USA | 750 | 3,750 | 1,088 | 1,088 | 2010 |
| Turk (AEP) | USA | 650 | 4,000 | 1,100 | 1,100 | 2011 |
| Big Stone 2 (Multiple) | USA | 630 | 3,600 | 1,080 | 1,080 | 2012 |

Note:  AEP Turk plant has claimed to be Ultra-Supercritical

Representative Advanced Supercritical Plants around the World

Note:  These plants claim to be Ultra-Supercritical

Cycle Design Optimization

In order to obtain the best overall Steam Turbine efficiency, several optimized cycle configurations and steam conditions for both Supercritical and Ultrasupercritical projects are shown in the following graphs.  The analysis assumed a 600 MW plant net power output and varying the main steam pressure and the main/reheat steam temperatures.  The pressure range was set from 3,500 psia to 4,500 psia and the main steam/reheat temperatures from 1,000 0F / 1,0000F to 1,300 0F / 1,300 0F.

Ultrasupercritical Ongoing and Future Material Developments

The key to further commercial advancements in steam cycles is the development of cost-effective alloys that have a higher corrosion resistance to higher steam temperatures and pressures.  The current design condition limitation is at or just above the 1,100 0F main steam/reheat steam temperature range.  However, for bituminous coals such as Illinois Basin, the current design condition limitation may be more restrictive.  This is due to the higher sulfur and chloride contents in the bituminous coals that lead to a much higher corrosion at higher main steam/reheat steam temperatures.  There are several risk factors that affect and drive the design considerations such as coal ash corrosion, steam side oxidation, dissimilar metal weld failure, long-term creep and availability risk.

Currently, material development programs have been established in Japan, the United States, and Europe to research and develop materials that would accommodate thermal cycling at higher steam conditions while maintaining plant reliability.  Initially, EPRI and the Electric Power Development Company (EPDC) programs focused on improving the high temperature-resistant ferritic-matrensitic 12CrMoV steels.  Operating temperatures of 1,100 0F were the initial target.

Further advancements in the United States of high temperature resistant austenitic steels are targeting steam conditions of 5,000 psi and 1,400 0F.  The work is being pursued as a consortium led by the National Energy Technology Laboratory.  Work is proceeding on both boiler and steam turbine technology development.

1. “Advancing Toward Ultrasupercritical Steam Cycles,” Sam Scupham and Schalk Van Der Merwe, Black & Veatch Holding Company, August 2007.

2. “Steam Turbine Design Considerations for Supercritical Cycles,” Justin Zachary, Paul Kochis, Ram Narula, Bechtel Power Corporation, August 2007.

3. “A Comparison of Integrated Gasification Combined Cycle (IGCC) and Supercritical Pulverized Coal (PC): 2007 Update,” Bob Slettehaugh and Anthony F. Black, Black & Veatch Holding Company, August 2007.

CCS PERFORMANCE AND COST ADDERS

# PUMPED STORAGE HYDRO

## Description

Pumped Storage Hydro (PSH) is a type of hydroelectric power generation that allows energy to be stored by pumping water into an elevated reservoir (Upper Reservoir).  Later, the stored water is used to generate power using a hydroelectric turbine generator as the water flows back down to a second reservoir (Lower Reservoir).  Reversible pump/turbine and motor/generator assemblies that act as both a pump and a turbine allow these two functions to be performed by one common set of equipment.

## performance and cost

Typically, water is pumped up to the Upper Reservoir for storage during the night and on weekends using low-cost energy, and the stored water is released to generate power during periods of high demand to displace high-cost generation.  As a result, much of the PSH value is derived from peak/off-peak price differentials.  PSH stations are actually a net consumer of electricity, as they consume 1.25 MWH of energy for every 1 MWH they produce.  Overnight cost is estimated to be in the range of $REDACTED/kW to $REDACTED/kW.  Upcoming geological studies should narrow this range.

PSH is the largest-capacity and one of the most cost-effective forms of grid energy storage available.  800-1600 MW facilities are being considered.  In addition to converting low-value off-peak energy into high-value peak energy, PSH systems also provide ancillary electrical grid services such as network frequency control and reserve generation.  PSH facilities can help to levelize system load and mitigate loading issues during off-peak periods for baseloaded coal and nuclear units (bottoming out).  PSH could also facilitate the integration of large-scale variable renewable resources such as wind, which may be available during undesirable times (night).

Underground Reservoir Pumped Storage Hydro (URPSH) is a variation of PSH technology that utilizes an underground Lower Reservoir.  Overnight cost for URPSH technology is expected to be $REDACTED/kW to $REDACTED/kW or higher.

# COMPRESSED AIR ENERGY STORAGE

### Introduction

As wind and solar capacity continues to grow, CAES and other bulk energy storage technologies will increasingly be used to help balance electrical supply and demand. Power production from wind is highly variable and less predictable. Furthermore, high winds do not necessarily coincide with the peak electricity demand. This disparity between production and demand has renewed interest in using CAES as a cost-effective way to add wind and other intermittent power sources to the mix. CAES allows the compression of air and storage during off-peak hours, when supply is high and price is low. Then, during peaks, this stored air is extracted, preheated and expanded to generate electric power.

Potential advantages of a CAES plant are as follows:

- Power Arbitrage – buying inexpensive off-peak energy and selling higher-priced on-peak energy

- Load Regulation – depending on plant configuration, flexibility to provide load following in the range from 20% to 70% of the CAES plant capacity within ~3-7 minutes

- Synchronous Reserve – depending on plant configuration, sudden load response up to 70% of the CAES plant capacity within ~3-7 minutes

- Enhancement of operations and economics of renewable resources

- Reduction of natural gas consumption compared to simple cycle or combined cycle plants

- Green Energy – the CAES output power is generated without incremental fuel consumption over that of the CT

### State of the technology

Originally, the Compressed Air Energy Storage (CAES) technology was developed as a load management tool to increase load factor of baseload plants during off-peak hours and then utilize stored energy during peak hours. Two CAES plants have operated for many years, using excess electricity to compress air into underground salt caverns and then using the compressed air to power turbo-generators when demand and prices are high. Both plants use a single power train, with self synchronizing clutches, which are utilized to select whether motor/generator is to be used to drive the compressor or to generate power to the grid. The first CAES plant in the world was E.ON Kraftwerk’s 320 MW plant in Huntorf, Germany in 1978. The plant has an 80MW compressor, which can fill the salt caverns in 8 hours at an air mass flow rate at 106 kg/s while the 320 MW turbine operates for 2 hours at the air mass flow rate of 417 kg/s. The second CAES plant was built by Power South Energy Co-operative in McIntosh, Alabama, and went commercial in 1991and generates 110MW. Its design is similar to the Huntorf plant.  It takes about 41 hours to compress the air into caverns and the turbo-generator can then operate at full capacity for 26 hours. One difference, however, is that McIntosh plant recuperates the waste heat from the expanders and uses it to heat the compressed air, boosting the plant efficiency by almost 25%.  Both Huntorf and McIntosh plants have operated reliably for the long term. These two plants are first generation single-shaft multiple component turbo-machinery design with the following deficiencies:

- No flexibility for specific compressor and expander power requirements

- Operational and maintenance complications

- Restrictions for plant optimization for specific grid and economic requirements and specific storage parameters

Several second generation (CAES2) plant concepts provide flexibility to meet a variety of operational and economic conditions and alleviate these deficiencies. Based on the available technical information, the second generation F-Class CT based CAES concept with Bottoming Cycle Air Expander and Inlet Chilling (CAES-BCE-IC) is suitable for Southern Company needs because of the following reasons:

- The total plant capacity is close to the target range

- The fuel related heat rate is lowest among all options

- Energy ratio (kWh-in/kWh-out) is quite favorable

- Design is relatively simple

- CT modification or changes in the OEM permissives may not be required

This and other similar second generation CAES designs have been patented by Dr. Michael Nakhamkin.  In 2008, Public Service Electric & Gas and Dr. Nakhamkin formed a Joint Venture company (Energy Storage & Power LLC) to license second generation CAES technology in North America.

The major components of this second generation CAES plant are as follows:

- One GE7F.05 natural gas fired combustion turbine (205 MW)

- Multiple motor driven compressors with intercoolers (~183 MW)

- Multiple industrial air expanders driving electric generators (~308 MW)

- Recuperator utilizing the CT exhaust gas to preheat the stored compressed air upstream of the expanders (CT exhaust temperature ~1100F, Recuperator exhaust temperature ~ 170F)

- Below ground compressed air storage

The simplified schematic of the CAES-BCE-IC (Figure 1) illustrates the main features of the plant. During off-peak hours, motor-driven compressors utilize the wind or any other renewable or base load energy and store it in the form of compressed air in an underground reservoir. During peak hours, the stored air is extracted from the storage, preheated and expanded in the BCE to generate electric power. The BCE is optimized to have the exhaust flow equal to the CT inlet flow and the exhaust temperature of approximately ~50°F. The BCE exhaust is injected into the CT inlet. Since this CT inlet temperature will be lower than the summer ambient, the CT output, and therefore, the overall CAES plant output will be increased.

Figure 1

Below are some examples of recent developments:

- Earlier this year, Pacific Gas and Electric received federal funds for the first stage of a 300-MW CAES plant in Kern Co., CA.

- First Energy owns the rights to an abandoned limestone mine in Norton, Ohio, that has the potential of generating 2700-MW of electric generation.

- One demo plant (150MW-10hr) is planned to be built by New York State Electric & Gas using a salt cavern.

It should be noted that cost and performance data can vary significantly depending on the site conditions. By performing an engineering and cost trade-off study of available turbo-machinery (CTs, expanders and compressors), which includes the cavern solution mining costs for CAES caverns at different depths, and different max and min pressures, one can calculate the lowest cost of the overall CAES plant as a function of depth. The overall CAES plant capital cost (on a $/kW basis) can change by as much as 50% depending on selection of the cavern depth (which sets the max pressure the cavern can withstand). The cavern max pressure will then set the minimum pressure, air flow rate and many other thermodynamic parameters for the above ground CAES plant turbo-machinery.

There are three potential unit configurations (Figure 2) that can provide different capabilities for rapid startup of the CAES2 unit:

  - “Standard”- In this configuration there are no auxiliary burners of any kind.  The unit is started by starting the GT and when the exhaust heat starts to increase the temperature of the recuperator the expander is started.  Power becomes available at approximately 7 minutes after the start sequence is initiated. Once the GT is at full-speed-no-load conditions the turbo expanders can be quickly brought to about 60% of their rated power although some expander power is available before the GT is up to full speed.  The startup time is principally determined by the startup time of the gas turbine. It is estimated that power will be available in about 7 minutes after the start sequence is initiated.  The startup emissions are solely those of the gas turbine.

  - “Duct burners” - In this configuration low NOx duct burners are installed in the input to the recuperator on the GT side.  The DB’s are fired as soon as the GT is at sufficient speed to have purged the recuperator and is supplying sufficient air flow to support DB operation. These types of low NOx duct burners are commercially available and modular in configuration.  Given their very short time of operation we believe permitting should be fairly simple in most jurisdictions. It is estimated that power will be available from the expanders approximately 5 minutes after the start sequence is initiated.  The startup emissions are those of the gas turbine plus the duct burners. It is believed that DB’s are available with emissions of less than 9 ppm, corrected to 15%O2.  The DB’s are only operated for periods of less than 15 minutes during a fast startup and should have a very small annual tonnage contribution to the plant.  For a normal startup they would not be operated at all.

  - “In-line burners” - In this configuration, high pressure in-line burners are installed in the air supply from the compressed air storage between the recuperator and the turbo expander. In starting the unit the turbo expanders are started as soon as the high pressure compressed air line and the expanders are purged and the high pressure burners are fired.  This allows the turbo expanders to begin generating power before the GT is up to speed.  Their operation is phased out within a few minutes as the GT is brought on-line.  Power becomes available as soon as three minutes after the start sequence is initiated.  The disadvantage of this configuration is that custom designed high pressure burners are required.  These types of burners are not readily available and would need to be custom designed and fabricated.

With the in-line burner configuration it is also possible to have the turbo expanders continuously synchronized to the grid at a minimum power level and the in-line burners continuously fired.  This would permit the entire expander plant output capacity to be sold in the market as synchronous reserve.  It should be noted that there would be a continual usage of compressed air and natural gas required to accomplish this so it would need to be economically evaluated.   Permitting might also be more difficult.

Figure 2

### Plant Output and Heat Rate

Total Power (Net) From CAES Plant, MW: REDACTED

Heat Rate (HHV) of CAES Plant, Btu/kWh-Out: REDACTED

Energy Ratio of CAES Plant, kWh-In/kWh-Out: REDACTED

Compressor Capacity, MW’s: REDACTED

Max Pressure in Cavern, psia: REDACTED

Min Pressure in Cavern, psia: REDACTED

Note: The max and min pressures will enable the generation cycle to last REDACTED when the cavern starts to discharge at max pressure, and the compression cycle to get back from the min cavern pressure to the max cavern pressure to be REDACTED. Thus, each hour of compression at the max power of the compressors will produce one hour of generation, net, at max power, which is the max power from the CT and the max power from the Expander, minus about REDACTED MW of losses. Due to the nature of the preliminary analysis performed, the numbers stated above have an accuracy of about REDACTED%.

### TOTAL PLANT COSTS

|  | Per Kilowatt |
| --- | --- |
| Total Plant Cost | REDACTED |

#### Basis for Plant Costs:

The estimate was factored from our simple cycle reference plant estimates and available literature concerning CAES plant capital cost. The estimate does not include the following:

- Cavern Development

- Land Cost

- Gas Lateral to Plant Site

- Transmission Interconnect Cost (scope ends at high side of GSUs and Motors)

- Pre COD O&M Capital Cost

- Project Development/Permitting Cost

- AFUDC

- Escalation (costs are 2011 “overnight” dollars)

### O & M COSTS

#### Fixed O&M Costs

###### Factored from the IRP GTDB CT and CC FOM data

| $/kW-Yr | REDACTED |
| --- | --- |

#### Variable O&M Costs

###### From EPRI CAES Demonstration Newsletter, July 2010

| Mills/kWh | REDACTED |
| --- | --- |

### EMISSIONS

|  | Lbs/MMBtu-HHV |
| --- | --- |
| Sulfur Dioxide (SO2) | REDACTED |
| Nitrogen Oxides (NOx) | REDACTED |
| Particulate Matter (PM) | REDACTED |
| Carbon Monoxide (CO) | REDACTED |
| Volatile Organics (VOC) | REDACTED |

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| ### MAINTENANCE TIME (weeks/yr) | REDACTED |
| ### EQUIVALENT FORCED OUTAGE RATE (Includes forced outages, maintenance outages and deratings) | N/A |
| ### EXPENDITURE DATA ATTACHED? | REDACTED |
| ### XI. Project Schedule: A typical EPC schedule from Notice to Proceed (start of engineering/procurement) to COD is approx. REDACTED months including cavern development. Some conceptual engineering and permitting activities would occur prior to NTP. From construction mobilization (sitework/cavern mining & development) to COD is REDACTED months. |  |
| ### EXPECTED PLANT DEGRADATION | REDACTED |
| ### CAPITAL EXPENDITURE FOR MAINTENANCE | REDACTED |

BASE LOAD CIRCULATING FLUIDIZED BED BOILER POWER PLANT NOMINAL 600 MW

### GENERAL DESCRIPTION OF THE PLANT

The unit is based on a 600 MW Circulating Fluidized Bed Boiler Power Plant operating at 2400 psig, 1050 0F main steam and 1050 0F reheat steam.  Plant cost basis and features include:

- (2) sub critical, single reheat Circulating Fluidized Bed (CFB) boilers with SNCR

- An air quality control system (AQCS) including pulse jet type fabric filters and polishing scrubbers

- One (1) reheat condensing steam turbine generator set

- Surface condenser

- Multiple cell mechanical draft cooling tower

- Seven (7) stages of regenerative heating consisting of two (2) stages of high-pressure closed feedwater heaters

- One (1) open deaerating heater

- Four (4) low-pressure closed feedwater heaters

- Single chimney shell with a dual flue liners

- Coal unloading and reclaim system

- Limestone storage and reclaim system

- Makeup water treatment system

- Wastewater treatment and discharge systems

- Fly ash and bottom ash storage

- Ash conveying

- Fire protection system

- Instrument/service compressed air systems

- Potable water system and service water system

State of Technology

This is a mature technology and currently available.

### HEAT RATE AND OUTPUT DATA

Expected Unit Performance Plant Estimated Performance (New and Clean):

|  | Net Plant Heat Rate (HHV) Btu/kW-hr | Net Unit Output kW |
| --- | --- | --- |
| Valves Wide Open (VWO) – Lignite Coal | REDACTED | REDACTED |
| VWO – PRB Coal | REDACTED | REDACTED |
| VWO – Central Appalachian Coal | REDACTED | REDACTED |
| VWO – Illinois Basin Coal | REDACTED | REDACTED |

  - Generic Greenfield site.

  - Performance at 89°F and 65% relative humidity.

  - The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

Expected Unit Performance Plant Estimated Performance (Degraded):

|  | Net Plant Heat Rate (HHV) Btu/kW-hr | Net Unit Output kW |
| --- | --- | --- |
| VWO – Lignite Coal | REDACTED | REDACTED |
| VWO – PRB Coal | REDACTED | REDACTED |
| VWO – Central Appalachian Coal | REDACTED | REDACTED |
| VWO – Illinois Basin Coal | REDACTED | REDACTED |

  - Generic Greenfield site.

  - Performance at 89°F and 65% relative humidity.

  - The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

  - Degradation of REDACTED% Output and REDACTED% Heat Rate.

### III.	TOTAL PLANT COSTS

Nominal 600 MW Site (New and Clean):

|  | $ Per Kilowatt | Total $ |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner’s | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

Basis for Plant Costs:

  - Generic Greenfield site.

  - Plant costs are overnight costs as of 1/1/12.

  - Site cost and owner’s cost assumed to be the same as that required for a Pulverized Coal Unit.

  - Refer to scope definition and exclusions in the Introduction section of the IRP Technology Data Book.

  - Costs per kW are calculated while using lignite fuel.  The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

Nominal 600 MW Site (Degraded):

|  | $ Per Kilowatt | Total $ |
| --- | --- | --- |
| EPC | REDACTED | REDACTED |
| Site | REDACTED | REDACTED |
| Owner’s | REDACTED | REDACTED |
| Total Cost | REDACTED | REDACTED |

Basis for Plant Costs:

  - Generic Greenfield site.

  - Plant costs are overnight costs as of 1/1/12.

  - Site cost and owner’s cost assumed to be the same as that required for a Pulverized Coal Unit.

  - Refer to scope definition and exclusions in the Introduction section of the IRP Technology Data Book.

  - Costs per kW are calculated while using lignite fuel.  The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

  - Degradation of REDACTED% Output and REDACTED% Heat Rate.

### IV.	O&M COSTS

#### Fixed O&M Costs (New and Clean)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (New and Clean)

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

  - Costs per kW are calculated while using lignite fuel.  The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

#### Fixed O&M Costs (Degraded)

###### (Based on the Peaking Rating)

| $/kW-Yr | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Variable O&M Costs (Degraded)

###### (Based on the Annual Average Rating and a REDACTED% Capacity Factor)

| Mills/kWh | REDACTED |
| --- | --- |
| Total/Yr | REDACTED |

#### Basis for O&M Cost Data:

Capacity factor of REDACTED%.

REDACTED starts per year.

O&M costs are in 1/1/2012 dollars.

Costs per kW are calculated while using lignite fuel.  The technology is capable of utilizing a variety of coal types, including PRB, CA, and Ill Basin.

Degradation of REDACTED% Output and REDACTED% Heat Rate.

### V.	EMISSIONS (Lignite Coal) (New and Clean)

|  | Lbs/MMBtu |
| --- | --- |
| Sulfur Dioxide | REDACTED |
| Nitrogen Oxide | REDACTED |
| Particulates – PM10 | REDACTED |
| Carbon Monoxide | REDACTED |

Basis for Emissions Data:

- Power Block Elevation: Approximately 450 feet above Mean Sea Level.

- Dry Bulb Temperature Design Value Median of Extreme Highs 91°F.

- Wet Bulb Temperature Design Value Median of Extreme Highs 79°F.

- Based on burning lignite coal.

| ### PLANT LIFE (yrs) | REDACTED |
| --- | --- |
| - MAINTENANCE TIME (weeks/yr) | REDACTED |
| - EQUIVALENT FORCED OUTAGE RATE (Includes forced outages/de-ratings and maintenance outages/de-ratings) | REDACTED |
| - EXPENDITURE DATA ATTACHED? | Yes |
| - PROJECT SCHEDULE ATTACHED? | Yes |
| - EXPECTED PLANT DEGRADATION | Output= REDACTED% Heat Rate = REDACTED% |
| - CAPITAL EXPENDITURE FOR MAINTENANCE ($/kW-yr) [Degraded values in brackets] | REDACTED |

## TECHNOLOGY FORECAST

#### PERFORMANCE PROJECTION:

| Widely Available Commercial Operation | Present | 2020+ |
| --- | --- | --- |
| Representative Technology: | Subcritical Steam Conditions, Boiler Size Limit (approx. 300 MW) | Supercritical Steam Conditions, Boiler Size Limit (approx. 600 MW) |
| Average Annual Heat Rate (New & Clean) | REDACTED | REDACTED |

## expenditure Data

The intent of the project expenditure data is to generically show when major expenditures (such as major equipment and construction costs) will happen, not to reflect all costs that may be necessary for a particular project.  Additional permitting, post-project invoice spending, or pre-project activities may not be shown.

Note: Minor project development expenses including air quality permit submittal begin approx. 1 year prior to Month 1 of this Expenditure Schedule.

|  | 600 MW CFB |  |
| --- | --- | --- |
|  | 2013 IRP Expenditure Curve | 2013 IRP Expenditure Curve (Cumulative) |
| Month |  |  |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED |
| 11 | REDACTED | REDACTED |
| 12 | REDACTED | REDACTED |
| 13 | REDACTED | REDACTED |
| 14 | REDACTED | REDACTED |
| 15 | REDACTED | REDACTED |
| 16 | REDACTED | REDACTED |
| 17 | REDACTED | REDACTED |
| 18 | REDACTED | REDACTED |
| 19 | REDACTED | REDACTED |
| 20 | REDACTED | REDACTED |
| 21 | REDACTED | REDACTED |
| 22 | REDACTED | REDACTED |
| 23 | REDACTED | REDACTED |
| 24 | REDACTED | REDACTED |
| 25 | REDACTED | REDACTED |
| 26 | REDACTED | REDACTED |
| 27 | REDACTED | REDACTED |
| 28 | REDACTED | REDACTED |
| 29 | REDACTED | REDACTED |
| 30 | REDACTED | REDACTED |
| 31 | REDACTED | REDACTED |
| 32 | REDACTED | REDACTED |
| 33 | REDACTED | REDACTED |
| 34 | REDACTED | REDACTED |
| 35 | REDACTED | REDACTED |
| 36 | REDACTED | REDACTED |
| 37 | REDACTED | REDACTED |
| 38 | REDACTED | REDACTED |
| 39 | REDACTED | REDACTED |
| 40 | REDACTED | REDACTED |
| 41 | REDACTED | REDACTED |
| 42 | REDACTED | REDACTED |
| 43 | REDACTED | REDACTED |
| 44 | REDACTED | REDACTED |
| 45 | REDACTED | REDACTED |
| 46 | REDACTED | REDACTED |
| 47 | REDACTED | REDACTED |
| 48 | REDACTED | REDACTED |
| 49 | REDACTED | REDACTED |
| 50 | REDACTED | REDACTED |
| 51 | REDACTED | REDACTED |
| 52 | REDACTED | REDACTED |
| 53 | REDACTED | REDACTED |
| 54 | REDACTED | REDACTED |
| 55 | REDACTED | REDACTED |
| 56 | REDACTED | REDACTED |
| 57 | REDACTED | REDACTED |
| 58 | REDACTED | REDACTED |
| 59 | REDACTED | REDACTED |
| 60 | REDACTED | REDACTED |
| 61 | REDACTED | REDACTED |
| 62 | REDACTED | REDACTED |
| 63 | REDACTED | REDACTED |
| 64 | REDACTED | REDACTED |
| 65 | REDACTED | REDACTED |
| 66 | REDACTED | REDACTED |
| 67 | REDACTED | REDACTED |
| 68 | REDACTED | REDACTED |
| 69 | REDACTED | REDACTED |
| 70 | REDACTED | REDACTED |
| 71 | REDACTED | REDACTED |
| 72 | REDACTED | REDACTED |
| 73 | REDACTED | REDACTED |
| 74 | REDACTED | REDACTED |
| 75 | REDACTED | REDACTED |
| 76 | REDACTED | REDACTED |
| 77 | REDACTED | REDACTED |
| 78 | REDACTED | REDACTED |
| 79 | REDACTED | REDACTED |
| 80 | REDACTED | REDACTED |
| 81 | REDACTED | REDACTED |
| 82 | REDACTED | REDACTED |
| 83 | REDACTED | REDACTED |
| 84 | REDACTED | REDACTED |
| 85 | REDACTED | REDACTED |
| 86 | REDACTED | REDACTED |

## indicative project schedule

REDACTED

FUTURE COMBINED CYCLE TECHNOLOGY WHITE PAPER

Advanced Combustion Turbine / Combined Cycle Technology

REMAINDER OF REPORT REDACTED IN ITS ENTIRETY