An Economic Study

of the

System Planning Reserve Margin

for the

Southern Electric System

December 2012

# EXECUTIVE SUMMARY

Because electric utility customers expect and depend on high levels of service reliability, a prudent utility must have an economically balanced level of generating capacity in excess of the upcoming season’s peak load.  To have this reserve capacity available when it is needed, a utility must plan much further beyond the upcoming season because processes to procure extra capacity, such as building a new unit or completing a power purchase agreement (PPA), take four years or more to complete.  The purpose of this reserve margin study is to determine the amount of reserve capacity that should be targeted four years in advance given the long lead time required for adding capacity. The three primary reasons for having this reserve capacity are:

- Weather: Projections of load are based on average weather.  If the weather is hotter than expected, the load will be higher.  In the Southern Company system, a load can be as much as 8% higher in a hot year than in an average year.  Drought conditions and temperature related derates of units can also significantly affect the load and capacity balance.

- Economic Growth Uncertainty: It is impossible to predict exactly how many new customers a utility will have or how much power existing customers will use from season to season.  Based on historical predictions and actual economic growth, loads may grow by as much as 5% more than expected during the four years required to procure new resources.

- Unit Performance: While the Southern Company system has a tremendous track record in keeping very low forced outage rates, there have been occasions when as much as 8% of the capacity of the system has been in a forced outage state concurrently.

Any one of these three factors creates a need for capacity reserves, however a more significant risk to consider is in the event of overlap of these components.  In such an event, more than 25% capacity reserves would be required to meet customers’ load demands plus operating reserve requirements at all times.  However, maintaining such high levels of capacity reserves comes at significant expense and may only eliminate very low probability events.  A more appropriate approach to setting the optimum target reserve margin is balancing the costs of maintaining reserves with the societal cost of not being able to serve all load demands and the cost of making expensive market purchases (reliability and emergency purchases).  This economic approach allows customers to have a high level of generation reliability and low electric tariffs at the same time.

In order to understand and quantify the overlap of the three contributing factors to the need for reserve margins, a system dispatch model named Strategic Energy and Risk Valuation Model (SERVM) is utilized.  SERVM evaluates the ability of the Southern Company capacity resources to meet load obligations for every hour in the year for thousands of draws of weather, load forecast error, and unit performance.  The model quantifies, in dollar cost, the impacts of three different components of unreliability.  These components are:

- Energy costs greater than the cost of a  combustion turbine (reliability purchases)

- Purchasing energy during emergencies (emergency purchases)

- Shedding firm load customers (expected unserved energy (EUE))

The analysis is performed on a range of planning reserve margins from 10% - 20%.  With lower reserve margin levels, the reliability costs are high and vary widely, but the carrying costs of reserves are low.  At higher reserve margin levels, the reliability costs are low, but the carrying costs of reserves are very high.  The objective of the study is to find the reserve margin target where these costs are minimized (i.e. the minimum cost point).  The “U” curve in the following figure shows the weighted average costs at each reserve margin level studied and demonstrates that a minimum total system cost occurs at 14%.

Figure 1: Optimum System Reserve Margin

REDACTED

While the minimum cost falls at 14%, the balancing of costs is between components with very different risk characteristics. Procuring capacity under a long-term PPA or building a new unit results in very static reliability costs. Typically, the only portion of carrying costs that are not stable are labor costs, which represent a small percentage of the total carrying costs. On the other hand, market purchases are very volatile from year to year depending on weather, load forecast error and system unit performance. The chart above represents the weighted average costs, while the chart below demonstrates the level of variation from weather and load forecast error.

Figure 2: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets

REDACTED

The trade-off, then, between static capacity costs and highly volatile reliability costs is difficult to measure. The approach taken to account for this inherent difference is to evaluate the risk using the risk metric, Value at Risk (VaR) at confidence levels between 85% and 95%. Value at Risk was calculated by subtracting the average cost from each specific scenario's cost. For a number of mild weather or slow load growth scenarios, the total cost was lower than average. For the extreme cases, the scenario cost was much higher than average. The 85% confidence VaR represents the total cost in the 85% case minus the average cost. The table below shows that to move from a reserve margin target of 14% to 15% would raise average system costs by $2M. However, by doing so, the Company can reduce risk from $117M to $100M at 85% confidence and from $335M to $294M at 95% confidence. This general risk trade-off can be seen in the flatness of the total cost “U” curve near the optimum point; a reserve margin a few percentage points higher than the optimum reserve margin would not cost much more on average, and would eliminate a number of expensive scenarios.

Table 1: Value at Risk

| Reserve Margin | Weighted Average ($M) | VaR 80 ($M) | VaR 85 ($M) | VaR 90 ($M) | VaR 95 ($M) |
| --- | --- | --- | --- | --- | --- |
| 10% | 346 | 171 | 255 | 410 | 712 |
| 12% | 307 | 111 | 152 | 246 | 489 |
| 14% | 293 | 69 | 117 | 182 | 335 |
| 15% | 295 | 59 | 100 | 164 | 294 |
| 16% | 300 | 49 | 91 | 146 | 250 |
| 18% | 321 | 40 | 61 | 111 | 176 |
| 20% | 351 | 28 | 49 | 84 | 153 |

Taking the optimum base case results and the risk metrics into account supports maintaining a reserve margin target of 15% for the long term. For shorter term planning (inside 3 years), a sensitivity has been performed which recognizes that there is typically smaller economic uncertainty. This sensitivity shows an optimum reserve margin of 13% and after considering risk, supports maintaining a minimum reserve margin of 13.5% for time periods inside 3 years. These recommendations are designed to provide guidance for resource planning decisions but should not be considered absolute targets. As explained throughout this report, various factors may justify decisions that result in reserve margins above or below the targets mentioned above such as: the large size of capacity additions, the availability and price of market capacity, or economic and political changes.

Significant changes to the modeling process were incorporated into the 2012 Reserve Margin study.  New logic and data were incorporated into SERVM, which allowed for improved assumptions to be made regarding dependence on energy markets, enhanced load modeling, water temperature derating, and load forecast error distribution.  The following provides more detail into the business logic changes in this study:

- Market modeling: Substantial enhancements were made to the regional modeling capabilities of SERVM since the last reserve margin study. In previous studies, the representation of the market was simplified. Neighboring utilities' loads had the same shape as Southern Company. The peak loads for all regions occurred in the same hour. Unit modeling was also relatively simplified. Because it did not differentiate capacity by its characteristics, it could not accurately capture the frequency or price at which energy was being sold between regions when reliability was not a significant concern. The enhanced version of SERVM utilized in this study models distinct load shapes for each region (by modeling each weather year and using the actual historical temperature and related load diversity for each region) and models the regions' actual units with their discrete characteristics. While the previous approach adequately captured the physical reliability benefits, the new logic better captures the full range of economic benefits of incremental efficient combustion turbines (CTs). The net effect of this change is to increase the value of incremental capacity and thus leads to a higher target reserve margin as a base case.

- Risk Analysis: The previous reserve margin study attempted to address risk by applying conservative assumptions on various inputs including market prices, the cost of EUE, neighboring reserve margins, and unit performance. The risk approach employed in this study attempts to make expected case assumptions on the inputs and apply conservatism to the selection of a reserve margin target.

- Load modeling: Hot and cold weather correlations in previous reserve margin studies tended to slightly underestimate the hot weather peaks and cold weather peaks.  The updated load model predicts slightly higher loads in hot weather periods and slightly higher loads in cold weather periods.  The tendency of this change is to slightly increase reliability costs and slightly increase the optimum reserve margin.

- Water Temperature Derating:  The SERVM database was updated to reflect water temperature derating of certain units more accurately.  In the previous study, approximately 630 MW were derated for the entire months of July and August for hot weather years.  Analysis of operational practices for recent drought years, particularly the extreme conditions during the summers of 2007 and 2008, and changes to the system related to the Utility MATS rule, revealed that the previous derating assumptions were too high.  The updated derating assumptions, consistent with actual practice, total approximately 200 MW for some of the hottest weather years on record.  This change reduces reliability costs and reduces the optimum reserve margin.

- Load Forecast Error:  In the previous reserve margin study, load forecast error was determined to be such that over-forecasting was more likely than under-forecasting.  The load forecast error has been reevaluated since the last study was performed.  The results show that while over-forecasting in the current study has a different probability distribution than over-forecasting in the previous study, the under-forecasting probability distribution has changed very little.  The vast majority of EUE cost and reliability and emergency purchase cost results from the under-forecasting cases.  Because the under-forecasting probability distribution has changed very little, there is very little impact on the optimum reserve margin. The maximum over-forecast error of 6.49% for the current study is higher than the maximum under-forecast error of -5.26%. This is still consistent with intuition, as load is typically reduced much more quickly than load is added.  In poor economic periods, customers go out of business or otherwise reduce load more quickly than when load is added during good economic periods.

The significant system changes that affected the results of this study include:

- The economic carrying cost of a CT in 2016 dollars decreased to $REDACTED/kW-year since the last study, which was $REDACTED/kW-year in 2016 dollars.  A lower CT cost results in a higher reserve margin for the minimum cost point.

- The system average peak Equivalent Forced Outage Rate (EFOR) has increased slightly since 2009.  Average system peak season EFOR for the period of study applicable to the previous reserve margin study was REDACTED%; for this study the average is REDACTED%.  Slightly higher EFOR results in slightly more reliability purchases and EUE, which results in a slightly higher reserve margin for the minimum cost point.

## TABLE OF CONTENTS

EXECUTIVE SUMMARY	i

TABLE OF CONTENTS	viii

LIST OF TABLES	ix

LIST OF FIGURES	x

I.  ASSUMPTIONS	1

A. Reliability Simulation Model	1

B. Market Modeling	2

C. Steam Unit Full Forced Outage Data	6

D. Steam Unit Partial Forced Outage Data	9

E. Combustion Turbine and Combined Cycle Outages and Capacity Ratings	9

F. System-Owned Conventional Hydro Generation	12

G. SEPA Conventional Hydro	14

H. Pumped Storage Hydro	15

I. Demand Side Management	15

J. Commitment	16

K. Dispatchers’ Peak Load Estimate Error	17

L. Weather Years	18

M. Unit Specific Adjustments Due to Weather Conditions	26

N. Load Forecast Uncertainty	26

O. Study Year	29

P. Capacity Cost	30

Q. Dispatch Order	30

R. Cost of Expected Unserved Energy	31

S. Planned Outage Patterns	32

II. SIMULATION PROCEDURE	34

A. SERVM Case Specification	34

B. Probabilities of Occurrence for Input Variables	35

C. Reliability Model Simulations	36

III. BASE CASE RESULTS	40

A. Key Drivers	40

B. Regional Capacity	41

C. Weather Diversity	42

D. Load Growth Uncertainty	42

E. Market Clearing	42

F. Unit Performance	42

G. Risk Analysis	43

H. Reliability Metrics	45

IV.  SENSITIVITY ANALYSIS	51

A. 50% Higher EFOR	51

B. No Weather Diversity	51

C. 50% Reduced Transmission	51

D. Capacity Cost Sensitivity	52

E. 50% Reduced Market Price	53

F. Higher Regional Reserves	53

G. Short Term Load Forecast Error	53

V.  CONCLUSION	54

A. Optimum System Planning Reserve Margin	54

VI. SUMMARY	56

## LIST OF TABLES

Table 1: Value at Risk	v

Table I.1: Simulation Regions Summary	3

Table I.2: Steam Unit Sample Seasonal Time to Failure and Time to Repair Data	8

Table I.3: System CT Ratings	10

Table I.4: System CC Ratings	12

Table I.5: Neighbor Demand Response Summary	16

Table I.6: Dispatch Peak Load Estimate Error	17

Table I.7: Annual Peak Load Variation	19

Table I.8: Annual Peak Load Variation Details (No Day of Week Adjustments)	19

Table I.9: Most Severe Summer Weather Years (No Day of Week Adjustments)	21

Table I.10: Peak Load Variation Details for Summer	22

Table I.11: Most Severe Winter Weather Years (No Day of Week Adjustments)	24

Table I.12: Peak Load Variation Details for Winter	24

Table I.13: Load Forecast Error	28

Table I.14: CT Cost Estimations	30

Table I.15: EUE Cost	31

Table I.16: EUE Cost Comparison	32

Table II.1: SERVM Case Variables	34

Table II.2: Annual EUE with 2.69% LFE	35

Table II.3: Input Variable Probabilities	36

Table II.4: Cases for Specific Reserve Margin	36

Table II.5: Sample Calculation of EUE at 10% Reserves	38

Table II.6: Sample Calculation of Purchases at 10% Reserves	38

Table III.1: Value At Risk	45

Table IV.1: Short Term Load Forecast Error	53

## LIST OF FIGURES

Figure 1: Optimum System Reserve Margin	iii

Figure 2: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets	iv

Figure I.1: Simulation Topology	4

Figure I.2: Scarcity Pricing Curve	5

Figure I.3: Unplanned Outage Probability	7

Figure I.4: Hydro Energy Availiability	13

Figure I.5: Annual Scheduled Hydro Energies	14

Figure I.6: Load Forecast Error Distribution Comparison	29

Figure I.7: Planned Outages…………………………………...……………………………………………33

Figure II.1: Variable Calculation Formula	37

Figure III.1: Optimum System Planning Reserve Margin	40

Figure III.2: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets	43

Figure III.3: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets:      . .         Top 10%	44

Figure III.4: Capacity Cost	46

Figure III.5: Expected Unserved Energy	47

Figure III.6: Loss of Load Equivalent	48

Figure III.7: Expected Unserved Energy Cost	48

Figure III.8: Purchase Energy	49

Figure III.9: Purchase Energy Cost	50

Figure IV.1: Reserve Margin as a Function of Capacity Cost	52

Figure V.1: Optimum System Planning Reserve Margin	54

Figure V.2: Economic Components of Reserve Margin	55

# I.  ASSUMPTIONS

The following sections of this report (A - S) provide detailed discussions related to the input assumptions associated with the review of Southern Electric System (“System”) generation reliability.  These discussions include the following:

- an overview of the simulation model used

- the representation of the performance of generating resources including hydro, steam, and peaking units, as well as load management and power purchase performance

- the development of  load representation adjusted for weather variations

- the applicable weather/hydro dataset

- appropriate costs to be utilized in the economic analyses of System generation reliability.

## Reliability Simulation Model

The Strategic Energy and Risk Valuation Model (SERVM) was used to determine EUE and reliability and emergency purchases.

SERVM randomly selects operating events from actual operating history to determine generating unit availability.  For each hour in each iteration, each unit will either be operating, on reserve shutdown, partially failed, completely failed, or on scheduled maintenance. The model calculates the total capacity online and compares it to the load to calculate associated EUE.  Performing the unit status random draws for 50 iterations for each hour of the dataset results in average or expected case EUE.  These unit modeling techniques are by far the best available for estimating system generation reliability.

There is, however, one important limitation to the model.  SERVM perfectly matches load and generation, which is impossible to do in the real world.  Every MW of load above the available capacity is calculated as EUE, but no adjustment is made for shedding more load than would actually be required.  In actual practice, load would be curtailed in large blocks and would be off longer than necessary.  This limitation was partially offset by modeling an operating reserve target greater than the requirement.

## Market Modeling

One of the primary new components of SERVM that was utilized for this study was enhanced region modeling. Previous implementations of the model only allowed for simplified representations of each of Southern’s neighbors to determine the expected support that they could provide. The load for each neighbor was perfectly correlated with Southern’s load. When Southern Company was at peak, all neighbors were at their peak also. This tended to overstate unserved energy and reliability costs because neighbors were unable to provide support since their loads were peaking in the same hours. The updated model allows Southern to accurately account for expected support from neighbors based on historical load diversity. Each weather year modeled uses the actual historical temperature and related load diversity for each region. In addition to a simple view of neighbor loads, the previous version of SERVM only used generic units for neighbors. There was no differentiation in cost or operational flexibility, or outage characteristics for any unit. The new version simulates the actual operation of each unit for every neighbor in the same way that resources are modeled within Southern. Hydro, CTs, base load thermal resources, as well as demand response resources are discretely modeled so that SERVM will produce an accurate hourly market price forecast. Since most regions have a significant percentage of resources with high dispatch costs, the efficient CTs added as marginal units to the Southern Company system are used frequently to avoid purchasing from neighbors at high costs.

To validate that the model accurately reflected the value of these efficient turbines, the output of the model was calibrated to recent history using actual market purchases. In recent years, regional reserves have been high and market prices have been depressed. However, because of the benefits of regional diversity, Southern Company was able to purchase several hundred thousand MWhs of energy at prices above the dispatch cost of a CT, but below the cost of old CTs or oil units that might have been run in the absence of energy from the market. SERVM was calibrated to produce a similar magnitude of purchases at similar prices. For the study year, the regional reserves were adjusted down to reflect published reserve margin targets for each of the regions modeled. Most of the neighboring regions use a 15% reserve margin target. Utilities in Florida target a 20% reserve margin. With lower reserves, purchases are expected to occur at higher prices. The simulations for the study year reflect the higher expected costs.

The regions used in the simulation are summarized in the table below:

Table I.1: Simulation Regions Summary

| Region Name | Reserve Margin Target (%) | Peak Load (MW) | Energy Limited Resources (MW) | Average Transfer Capability into Southern (MW) | Average Total Transfer Capability with all Neighbors (MW) | CBM* into Southern (MW) |
| --- | --- | --- | --- | --- | --- | --- |
| TVA | 15% | 35,000 | 7,018 | 1,207 | 4,669 | 400 |
| Duke | 15% | 32,450 | 4,488 | 432 | 2,468 | 350 |
| SCEG | 15% | 5,138 | 976 | 176 | 1,616 | 75 |
| Santee Cooper | 15% | 5,155 | 553 | 120 | 3,070 | 125 |
| FPL | 20% | 23,835 | 1,802 | 79 | 2,688 | - |
| Progress FL | 20% | 11,415 | 981 | 218 | 1,443 | - |
| JEA | 20% | 3,145 | - | 74 | 1,401 | - |
| TAL | 20% | 578 | 38 | 22 | 188 | - |
| AEC | 15% | 2,369 | 63 | Not Limited | Not Limited | - |
| Entergy | 15% | 16,112 | 1,124 | 1,576 | 3,367 | 100 |
| SMEPA | 15% | 1,555 | - | ### 423 | ### 700 | ### - |
| ### OPC | ### 15% | ### 7,636 | ### 702 | ### Not Limited | ### Not Limited | ### - |
| ### MEAG | ### 15% | ### 2,269 | ### - | ### Not Limited | ### Not Limited | ### - |

*Capacity Benefit Margin (CBM) is a firm import reservation on the transmission system for use during emergencies.

The topology used for the simulations is in Figure I.1.

Figure I.1: Simulation Topology

SERVM simulates sales and purchase transactions between any region when the market price in one region is higher than an adjoining region and there is sufficient transfer capability. The model attempts to capture all transactions that occur at prices above the cost of an efficient CT. During extreme scenarios when loads are high and many units are in a forced outage state, prices can rise substantially higher than the cost of a CT. The scarcity pricing curve in the model used to estimate these costs was developed using 10 years of historical market purchases and is shown in the figure below. Scarcity prices could rise as high as $10,000/MWh if a region is in an emergency situation and is about to shed firm load. These types of events are extremely rare in the simulation and in actual practice.

Figure I.2: Scarcity Pricing Curve

During emergency conditions, SERVM attempts to procure as much energy from the marketplace as possible and will call on other peaking resources such as interruptible customers, voltage control, and emergency hydro. If the system is still short the necessary capacity to meet load plus operating reserves, SERVM will call CBM. Southern Company has CBM reservations on ties with TVA, Duke, Entergy, South Carolina Gas and Electric, and South Carolina Public Service Authority totaling 1,150 MW. Since CBM can be used non-firm, the model may have already utilized the transmission capacity on a non-firm basis prior to calling CBM, so the net effect of calling CBM may be zero in some hours.

*Capacity Benefit Margin (CBM) is a firm import reservation on the transmission system for use during emergencies.

## Steam Unit Full Forced Outage Data

Generating units typically operate for a period of time, fail, are repaired, and then operate again.  For example, a unit may run from 500 to 1500 hours before it fails, take from 3 to 500 hours to repair, then run again for 500 to 1500 hours.

For each unit the simulation will randomly select failure events and operating events. Every hour certain units will be operating and other units will be in a failure state. The important aspect of reliability modeling is to capture time periods when a large number of units are in forced outage state. To ensure the model predicts these events accurately, a comparison was made of the simulated outage probability to the actual outage probability. Unplanned outage probabilities are shown in the following figure. It shows that when only considering forced outages and derates, 10% of all hours will have greater than 1,000 MW offline. When considering forced outages, derates and other unplanned outages, 10% of all hours will have greater than 1,700 MW offline. The difference between these two curves is made up of outages for which operators have some scheduling flexibility. In recent history, these flexible outages occurred on-peak because regional reserves were high and the capacity was not needed. In the future, some of these outages would be reserved for off-peak hours. The appropriate assumption to use in the model is that some of these flexible outages will occur on-peak while others will be scheduled for off-peak periods. As shown in the following figure, the SERVM calibrated outage curve falls in between the forced outage only and the total unplanned outage curves. This indicates that SERVM is adequately modeling the impact of outage events.

Figure I.3: Unplanned Outage Probability

Data is available that reflects each System generating unit’s historical operating performance.  An analysis of the data reveals that the steam units are approximately REDACTED% more reliable in July and August than the rest of the year.  The increased reliability stems from the high emphasis placed during the summer months on keeping the units running due to the increased customer demand.  In off-peak months, units might be placed on forced outage more quickly than they are during summer and winter months because the need to keep them operating is diminished.  These reasons for the higher summertime reliability are only conjecture, but actual higher availability (reliability) has been observed and documented in the past.  The 2012 study used fall 2006 through summer 2011 actual operating history data for each existing generating unit.  An examination of this data revealed a slightly lower availability of the System’s generating units than in previous studies.  The peak season EFOR used in this study is REDACTED%.  The 2009 Reserve Margin study used 2003 – 2008 operating history and showed a peak season EFOR of REDACTED%.  When this study is revised in the future, changing trends in unit reliability will need to be monitored because of their effect on EUE.

Forced outage and maintenance outage data for this study consists of a series of observations, based upon historical information.  This data is assembled into time-to-failure and time-to-repair distributions.  Time-to-failure and time-to-repair distributions were entered on seasonal bases.

Typical data for a unit might have up to two dozen entries in the time-to-fail (TTF) input data record parsed on seasonal bases, ranging from just a few hours to as many as 16,000 hours.  Likewise, the typical data will contain a corresponding amount of seasonal entries in the time-to-repair (TTR) distribution, ranging from one to 6600 hours.  As SERVM processes chronologically, it will randomly choose a TTF duration from the first data record and then randomly choose a TTR duration.  Individual unit operation, therefore, is a direct reflection of what has happened over the last five years.  Since units are independent of each other it is possible that many units can be down at once.  An example of this type of input data is given in Table I.2.

Table I.2: Steam Unit Sample Seasonal Time to Failure and Time to Repair Data

| Unit Name | Summer Time to Fail (hours) | Winter Time to Fail (hours) | Off-Peak Time to Fail (hours) | Summer Time to Repair (hours) | Winter Time to Repair (hours) | Off-Peak Time to Repair (hours) |
| --- | --- | --- | --- | --- | --- | --- |
| Sample Plant | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
|  | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |

Most steam units have their own specific history that is used in SERVM. Units without outage history were modeled by pointing to a similar unit that did have historical outage data.  Forced outage rates, ratios of failed hours to operating hours, or ratios of failed hours to total hours are outputs of SERVM rather than inputs.  The steam unit forced outage rates ranged from 0% to 11% in the summer, from 0% to 14% in the winter, from 0% to 33% in the off-peak periods and from 0% to 14% annually.

## Steam Unit Partial Forced Outage Data

Generating units periodically experience equipment failures, which require the units to operate at reduced output.  These partial outages are generally less significant than full forced outages but must still be considered when determining System generation reliability.

In contrast to the results of the full forced outage, some units were found to have slightly lower reliability in the summer months in terms of measuring partial outages only.  Partial outages occurred more frequently and were repaired more quickly in the summer.  One possible explanation for the difference may be that partial deratings do not occur as often in the non-summer months because the units are not called on for economic dispatch as often during that period.

Partial outages represent about one quarter of the total EFOR of the system; partial outages are modeled using the same rigorous approach that is used for full outages.  An entire distribution is built for TTF events, TTR events, and the percentage derate.  During the simulation, full outages and partial outages are tracked and randomly drawn separately.

## Combustion Turbine and Combined Cycle Outages and Capacity Ratings

CT units have TTF and TTR data in the form of real observations recorded in SERVM on seasonal bases.  Typical data for a unit might have 8-12 entries in the TTF input data records, ranging from just a couple of hours to as much as several thousand hours, and 8-12 entries in the TTR of smaller values.  As SERVM processes chronologically, it will randomly choose TTF duration from the first data record and then randomly choose TTR duration.  Individual unit operation, therefore, is a direct reflection of what has happened over the selected sample years of data.  In recent history, reserves in the region were robust and many of the older CTs in the fleet were not dispatched frequently. Some of these units had annual operating hours below 10 hours. For such a unit, a single forced outage event of 20 hours in duration would result in an EFOR of 66%. In scenarios with lower reserve margins, these units would dispatch more frequently and it is expected that they would be able to operate with an EFOR much better than 66%. With low gas prices and increased CT operating hours projected for 2016 and to prevent an improper impact of TTR and TTF values from low demand historical years, the EFOR for most CTs has been capped at 25%.  A small number of CTs have the EFOR capped at 20%.  Since units are independent of each other it is possible that many units can be down at once.  The CT unit forced outage rates ranged from 0.05% to 25% in the summer, from 0.19% to 25% in the winter, from 0.19% to 25% in the off-peak periods and from 0.19% to 25% annually.

Maximum unit capacity ratings for CTs are determined at the point on the capacity versus ambient temperature curve where the ambient air inlet temperature is 95°F.  Table I.3 identifies the approximate ratings of existing system CTs.  The capacities are derated for high ambient temperature as discussed in Section M.

Table I.3: System CT Ratings

| SYSTEM CT RATINGS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Unit Name | Rating (MW) |  | Unit Name | Rating (MW) |
| AM SYLAC 1 | 47.5 |  | MCGPC GT 2 | 82.2 |
| AM SYLAC 2 | 47.5 |  | MCGPC GT 3 | 82.2 |
| BLVRD GT 1 | 14.0 |  | MCGPC GT 4 | 82.2 |
| BLVRD GT 2 | 14.0 |  | MCSAV GT 5 | 82.2 |
| BLVRD GT 3 | 14.0 |  | MCSAV GT 6 | 82.2 |
| CALHO GT 1 | 158.0 |  | MCGPC GT 7 | 82.2 |
| CALHO GT 2 | 158.0 |  | MCGPC GT 8 | 82.2 |
| CALHO GT 3 | 158.0 |  | PEARIDGT 1 | 12.0 |
| CALHO GT 4 | 158.0 |  | PVMPC PU 1 | 150.5 |
| CHEVN GT 1 | 15.0 |  | PVMPC PU 2 | 158.0 |
| CHEVN GT 2 | 15.0 |  | PVWALTPU 1 | 149.0 |
| CHEVN GT 3 | 16.0 |  | PVWALTPU 2 | 149.0 |
| CHEVN GT 4 | 16.0 |  | PVWALTPU 3 | 148.9 |
| CHEVN GT 5 | 68.0 |  | PVWASHPU 2 | 154.6 |
| DAHLBERG 1 | 75.0 |  | PVWASHPU 3 | 155.0 |
| DAHLBERG 2 | 74.0 |  | SWEAT GT 1 | 30.0 |
| DAHLBERG 3 | 75.0 |  | WARPK GT 1 | 80.0 |
| DAHLBERG 4 | 75.0 |  | WARPK GT 2 | 80.0 |
| DAHLBERG 5 | 75.0 |  | WATSO GT 1 | 31.0 |
| DAHLBERG 6 | 75.0 |  | BOWEN OT 1 | 32.0 |
| DAHLBERG 7 | 75.0 |  | GASTO OT A | 16.0 |
| DAHLBERG 8 | 74.0 |  | INTER OT 1 | 140.9 |
| DAHLBERG 9 | 75.0 |  | MCMAN DS 1 | 2.0 |
| DAHLBERG10 | 75.0 |  | MCMAN OT 1 | 44.1 |
| EXHEARD 1 | 157.5 |  | MCMAN OT 2 | 44.1 |
| EXHEARD 2 | 157.5 |  | MCMAN OT 3 | 44.1 |
| EXHEARD 3 | 157.5 |  | MCMAN OT 4 | 44.1 |
| EXHEARD 4 | 157.5 |  | MCMAN OT 5 | 44.1 |
| EXHEARD 5 | 157.5 |  | MCMAN OT 6 | 44.1 |
| EXHEARD 6 | 157.5 |  | MCMAN OT 7 | 44.1 |
| GREEN CT10 | 85.0 |  | MCMAN OT 8 | 44.1 |
| GREEN CT 2 | 84.0 |  | MCMAN OT 9 | 44.1 |
| GREEN CT 3 | 82.0 |  | MITCH OT 1 | 31.0 |
| GREEN CT 4 | 81.0 |  | MITCH OT 2 | 31.0 |
| GREEN CT 5 | 82.0 |  | SMITH OT 1 | 32.0 |
| GREEN CT 6 | 81.0 |  | WANSL OT 1 | 27.0 |
| GREEN CT 7 | 80.0 |  | WILSO DS 1 | 2.5 |
| GREEN CT 8 | 83.0 |  | WILSO OT 1 | 44.0 |
| GREEN CT 9 | 82.0 |  | WILSO OT 2 | 44.0 |
| KRAFT CT 1 | 17.0 |  | WILSO OT 3 | 44.0 |
| MCDON GT 1 | 32.0 |  | WILSO OT 4 | 44.0 |
| MCDON GT 2 | 32.0 |  | WILSO OT 5 | 44.0 |
| MCGPC GT 1 | 82.2 |  | WILSO OT 6 | 44.0 |

Southern Company’s combined cycle units have been in commercial operation for as much as 12 years and have adequate outage data available.  For example, McIntosh 11 has a mean time to failure of REDACTED hours and a mean time to repair of REDACTED hours.  Additionally, in real-time operations, the supplemental modes (i.e. full pressure (FP) and power augmentation (PA)) of a CC are dispatched separately from the base operating mode.  The supplemental modes have a higher heat rate value and, therefore, are dispatched during the same demand periods as CTs.  SERVM provides the flexibility to model the supplemental modes separately from the base operating mode; therefore, they are modeled as CTs in this study.

Capacity ratings for CCs are also determined at the point on the capacity versus ambient temperature curve where the ambient air inlet temperature is 95°F. Table I.4 identifies the approximate ratings of existing system CCs currently in service or modeled for service in 2016.  The capacities are derated for high ambient temperature as discussed in Section M.

Table I.4: System CC Ratings

| SYSTEM CC RATINGS |  |
| --- | --- |
| Unit Name | Rating (MW) |
| BARRY 6 | 532.0 |
| BARRY 7 | 532.0 |
| DANIEL 3 | 502.0 |
| DANIEL 4 | 500.0 |
| HARRIS 1 | 638.2 |
| HARRIS 2 | 630.5 |
| MCDONO 4 | 836.0 |
| MCDONO 5 | 836.0 |
| MCDONO 6 | 836.0 |
| MCINT 10 | 628.4 |
| MCINT 11 | 628.2 |
| SMITH 3 | 556.0 |
| WANSL 6 | 568.4 |
| WANSL 7 | 575.5 |

## System-Owned Conventional Hydro Generation

The use of a chronological, Monte Carlo-based model for system simulation is necessary to determine the reliability impact of conventional hydro generation.

A System-owned hydro capacity of REDACTED MW (projected for the year 2016) was divided into three components:

- Run-of-River (ROR) Hydro

- Scheduled Hydro

- Emergency or “Unloaded” Hydro

This study includes 50 different hydro scenarios that are matched with the 50 weather scenarios.  The 50 scenarios chosen are based on the past 50 years (1962-2011) of weather and hydro data.  For each of the scenarios, ROR and scheduled hydro capacity are modeled based on actual history.  As in previous updates, the ROR capacity operates in every hour and varies for each month of the year.

The hydro simulation logic takes into account that the optimal dispatch of hydro resources is not simply an economic decision.  Planners must take into account river flow requirements and impacts on other reservoirs in the same river system.  During drought conditions, it is rare that the full capacity of all hydro resources would be dispatched at the same time.  In the model, the total hydro capacity that was not used in scheduled or ROR would be available as emergency hydro.  Only in cases of extreme need will the emergency hydro capacity be called to operate. Also, the emergency hydro block is only available for a small number of events per year. The emergency hydro block is tied to a flex energy account to reflect its energy limitations. If the emergency capacity is needed rarely, the model will pull energy from this account to meet loads during emergencies. If the capacity is needed frequently, the energy account may become depleted and the capacity may not be available during emergencies.

Figure I.4 depicts average flow information for an average year (1998) that can be expected over twelve months for the three components of System-owned hydro generation.  The figure illustrates how hydro energy availability may typically occur in an average year when comparing the ROR and scheduled capacity columns.  The total monthly energy, which is represented as the height of the bar, is the sum of ROR energy and dispatchable energy.  The dispatchable energy is the sum of scheduled and emergency hydro energies.

Figure I.4: Hydro Energy Availiability

Development of Hydro Patterns

Typically, the summer months yield varying weather and hydro conditions in the southeastern United States that influence the peak and energy demands across the System.  Being a predominately summer-peaking utility system, the System has significantly higher peaks and energy demand, and subsequently potential for periods of EUE, during the hotter summer months due to the higher temperatures.

As with the weather data, the availability of hydro can vary year to year and can affect generation reliability.  Figure I.5 illustrates the total available scheduled hydro energies from the past 50 weather years (1962-2011).

Figure I.5: Annual Scheduled Hydro Energies

## SEPA Conventional Hydro

The Southeastern Power Administration (SEPA) conventional hydro is less flexible in its operation than the System-owned hydro, but due to the updated hydro logic in SERVM, the same variables are used to model SEPA hydro.  The System has a contractual right to REDACTED MW taken over four hours per weekday.  This equates to REDACTED megawatt-hours per weekday of SEPA hydro from the large projects, with a maximum operation of REDACTED MW.  Energy can be taken over longer periods of time, meaning less than REDACTED MW is taken in each hour.  In the current study, SEPA conventional hydro is modeled as a standard hydro unit with minimum daily dispatches.

The option to retain SEPA conventional hydro for use later in the week is sometimes available, but it is not a dependable option.  This option is ignored, and to the extent that it might be available, this modeling method is somewhat conservative (overestimating EUE).

## Pumped Storage Hydro

Pumped storage hydro is a resource that is designed to pump water to a higher pond using energy at off-peak periods when prices are low, and to generate electricity by releasing that water at times when prices are high. The dispatch of pumped storage is not simply a reliability decision, although the pond should always be kept at a level where energy will be available for emergency conditions. Enhancements were made to SERVM so that all pumped storage resources optimize the pumping schedule during low cost hours and generate during high cost hours. Southern Company has a total of 527 MW of pumped storage resources spread across two different locations (Wallace Dam and Rocky Mountain Pumped Storage Facility). The Rocky Mountain Pumped Storage Facility is shared with OPC. Other regions modeled including Duke, TVA, and SCEG also have pumped storage resources.

## Demand Side Management

Approximately REDACTED MW of demand side management (DSM) capacity is included in the analysis.  The load management resources include such programs as Interruptible Service (IS), Real-Time Pricing (RTP), Direct Load Control (DLC), and Stand-by Generation (SBG).  The actual contract amount of capacity (in MW) associated with each of these resources is input to SERVM.  Since the SERVM model includes the contract constraints (e.g., hours per year, days per week, and hours per day) for these energy-limited resources, there is no need to adjust the contracts by multiplying by ICE factors.  (The “ICE” factor refers to “incremental capacity equivalent” factors).  In general, ICE factors represent the worth of load management resources, such as an interruptible service contract, relative to the value of incremental generating capacity that can be added to the system.

The following table summarizes the modeled demand side programs for neighboring utilities:

Table I.5: Neighbor Demand Response Summary

| NEIGHBOR DEMAND RESPONSE SUMMARY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Contract Description | Capacity (MW) | Hours Per Year | Hours Per Day | Days Per Week |
| AEC | 55 | 200 | 8 | 5 |
| Duke | 984 | 200 | 8 | 5 |
| Entergy | 969 | 200 | 8 | 5 |
| FPL | 2060 | 200 | 8 | 5 |
| Progress FL | 723 | 200 | 8 | 5 |
| Santee Cooper | 424 | 200 | 8 | 5 |
| SCEG | 225 | 200 | 8 | 5 |
| TAL | 38 | 200 | 8 | 5 |
| TVA | 1500 | 200 | 8 | 5 |
| TOTAL AVAILABLE CAPACITY: | 7822 MW |  |  |  |

These resources occupy specific positions in the dispatch order.  The position in dispatch affects their ability to reduce EUE and alters the frequency with which they are called.  Additionally, in real-time operations, the IS contracts are divided into three “blocks” and are called upon in a rotating manner to be equitable to each of the customers.  For example, a condition occurs in which the Company needs to call on IS customers to reduce demand, so the Company calls on Block A.  The next time a condition occurs where the Company needs to reduce peak demand, the Company will call on Block B.  SERVM provides the flexibility to model the IS contracts more closely with how they are called in reality than other reliability models do.

## Commitment

Resources in SERVM are committed to match the current operating practices.  Each week during the simulation, an algorithm looks at the loads for each hour of the week and sets the optimum dispatch in order to maintain the required operating reserves for every hour.  The optimum dispatch takes into consideration which units are available, the minimum uptimes and downtimes for each unit, and the startup costs and times for each unit.  The System always carries operating reserves of at least REDACTED MW.  This is approximately equal to the capacity of the largest unit in the control area, Plant Vogtle, which has REDACTED MW capacity.  This operating reserve is a requirement actively enforced by NERC.  If the load is higher than forecast, or if units fail between commitment periods and operating reserves are expected to be lower than the required minimum, SERVM will dispatch additional units to keep the System above the minimum required. In practice, because of load forecast error and the possibility of unexpected unit failures, the system will frequently keep more capacity available than the minimum requirement. SERVM attempts to mimic this accommodation for uncertainty and capture the costs of this imperfect knowledge.  The algorithms used in the current study turn off units when they are not needed during off-peak periods.

## Dispatchers’ Peak Load Estimate Error

The dispatchers' peak load estimate error is modeled in SERVM as a 21-step probability distribution of the error in the dispatchers' projection of the peak expected across the next two days.  The peak load error was developed from a comparison of actual loads to the dispatchers' short-term projections and is presented in Table I.6.

Table I.6: Dispatch Peak Load Estimate Error

| DISPATCH PEAK LOAD ESTIMATE ERROR |  |
| --- | --- |
| % Energy (1) | Probability (2) |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| REDACTED | REDACTED |
| Notes: (1) The percent that the forecasted peak differed from the actual peak (2) The probability that the forecasted peak would differ from the actual peak by the specified percentages |  |

The dispatchers’ peak estimate error does not have a significant effect on EUE.  Within a range of reasonable commitment levels, all steam units would already be committed on days when EUE is likely, so missing the forecast would not make large units unavailable during periods of high load.

## Weather Years

The unpredictability of weather affects generation reliability.  Historical weather patterns for 50 years (1962-2011) were utilized to develop the 50 load datasets used in this reliability analysis.  In general, if weather remains normal over time, concerns for system generation reliability are minimized.  However, if the System experiences many days with abnormal temperatures, System demand would increase significantly.  Naturally, extended abnormal temperatures (on the high side in the summer period and on the low side in the winter period) would increase the risks and potential for System generation-related reliability problems.  For this study, these 50 datasets were given equal probability of occurrence.  The same methods used in the 2009 study were used to develop the 50 weather load shapes (datasets) for the 2012 study.  Starting with a series of historical weathers and loads, a neural network program was used to develop relationships between a series of weather observations and load responses.  Once the neural network had developed the relationships (also known as being “trained”), the individual 50 weather load shapes were developed from the individual streams of temperature data.  This results in 50 datasets of load data. Because load is strongly influenced by whether extreme temperatures occur on a weekday or a weekend/holiday, each of these datasets are impacted by which day of the week starts the weather year.  The load datasets for the 50 weather years starting on Sunday, Monday, Tuesday, Wednesday, Thursday, Friday and Saturday were developed resulting in a total of 350 datasets (50 years × 7 start days). For the 2009 study, load data sets for 48 weather years starting on Monday were used.  Table I.7 shows for the five most severe weather years the percent deviation from the average peak load of datasets analyzed in the 2009 and 2012 studies with all weather years starting on Monday.  As shown in the table below, in datasets with the most severe weather, the peak can be as much as 7.05% higher than the average.  In contrast, the previous 2009 study showed that in datasets with the most severe weather, the peak can be as much as 6.52% higher than the average.

Table I.7: Annual Peak Load Variation

| PEAK LOAD VARIATION |  |  |
| --- | --- | --- |
| Weather/ Hydro Dataset | Deviation from Average (1) |  |
|  | 2009 Study | 2012 Study |
| 1 | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED |
| Notes: (1) The percent that the peak load differed from the study's average peak load with all weather years starting on Monday |  |  |

The load model not only differentiates between weekdays and weekends/holidays; it also differentiates among the five weekdays and between the two weekend days. For example, if the same temperatures occur on a Wednesday and Thursday, the Thursday peak load will be 0.8% lower than the Wednesday peak load.  In order to show the impact of just weather on load, all days of the year were specified to be Wednesday so that there would be no day of the week adjustment.  Note that the “all days are Wednesdays” is for illustration only; the SERVM model differentiates between days as described above.

The maximum annual peak load with no day of the week adjustment is in the winter of the 1966 weather year, and the second highest annual peak load is in the summer of the 1980 weather year. The annual peak load variations for the top 27 weather years as a percent deviation from the average of the annual peaks for all 50 weather years are shown below.

Table I.8: Annual Peak Load Variation Details (No Day of Week Adjustments)

| Year | Annual Severity Rank | Deviation From Average of Annual Peak Loads |
| --- | --- | --- |
| 1966 | 1st | 6.20% |
| 1980 | 2nd | 6.08% |
| 2003 | 3rd | 5.96% |
| 2000 | 4th | 5.69% |
| 2007 | 5th | 5.32% |
| 1985 | 6th | 5.13% |
| 1970 | 7th | 4.59% |
| 1994 | 8th | 3.58% |
| 1983 | 9th | 3.38% |
| 1986 | 10th | 2.88% |
| 1995 | 11th | 2.14% |
| 1968 | 12th | 1.84% |
| 1969 | 13th | 1.74% |
| 1982 | 14th | 1.18% |
| 2011 | 15th | 0.76% |
| 1999 | 16th | 0.39% |
| 1977 | 17th | 0.23% |
| 1990 | 18th | -0.07% |
| 1962 | 19th | -0.15% |
| 1965 | 20th | -0.22% |
| 1992 | 21st | -0.34% |
| 2010 | 22nd | -0.46% |
| 1979 | 23rd | -0.49% |
| 1964 | 24th | -0.50% |
| 2006 | 25th | -0.96% |
| 1981 | 26th | -1.04% |
| 1996 | 27th | -1.13% |

In order to reduce the SERVM run time to a manageable level, load datasets with only two of the seven start days for the 50 weather years were used in the 2012 study. Tuesday and Saturday start days were chosen for the reasons shown in the following paragraphs.

One reason for using Tuesday and Saturday is that the weather year 1966 with a Tuesday start day and the weather year 1980 with a Saturday start day covered the most severe winter and summer peak loads, respectively.

## Summer Peak Loads

The summer peak loads for the 350 datasets were ranked from high to low. The ranking was analyzed and it was determined that using the 50 weather years starting on Tuesday and Saturday and the associated 100 summer peak loads (50 years × 2 start days) was representative of the 350 summer peak loads. The top ten of the 100 peak loads for the “Tuesday and Saturday start day” sets and the top 41 of the 350 summer peak loads for the “all seven start day” sets occurred during the ten most severe summer weather years. For the ten most severe summer weather years, the percentage for the summer peak loads above the average of all 350 summer peak loads averaged 3.81% for Tuesday and Saturday start day sets and 3.92% for all seven start day sets.

The most severe summer weather years with no day of the week adjustment are shown in the following table. Note that the summer peak for 1980 of 6.96% above the average of summer peaks from all 50 weather years. This is considerably higher than the 6.08% shown in Table I.8 for the most severe summer weather year (the most severe annual weather year was winter of 1966 and the 2nd most severe annual weather year was summer of 1980) because the average of annual peak loads for 50 weather years was higher than the average of all 50 summer peak loads.

Table I.9: Most Severe Summer Weather Years (No Day of Week Adjustments)

| Weather Year | Summer Severity Ranking | Deviation From Average of Summer Peak Loads |
| --- | --- | --- |
| 1980 | 1 | 6.96% |
| 2000 | 2 | 6.56% |
| 2007 | 3 | 6.19% |
| 1970 | 4 | 5.46% |
| 1983 | 5 | 4.23% |
| 1986 | 6 | 3.21% |
| 1995 | 7 | 2.99% |
| 1968 | 8 | 2.68% |
| 1969 | 9 | 2.59% |
| 2011 | 10 | 1.60% |

The top 41 of the 350 peak summer loads for the all seven start day datasets are shown below.  Note that the 1980 year with a Saturday start day is the most severe and is over 8% above the average of all 350 peak loads.  This is considerably higher than the 6.08% above the average of all 50 annual peak loads shown in Table I.8 because the average of annual peak loads for 50 weather years with no day of the week adjustment was higher than the average of all 350 summer peak loads.

Table I.10: Peak Load Variation Details for Summer

| Summer Severity Rank | Summer Severity Year | Start Day for Year | Deviation From Average of All 350 Summer Peak Loads |
| --- | --- | --- | --- |
| 1st | 1980 | Saturday | 8.05% |
| 2nd | 1980 | Friday | 7.85% |
| 3rd | 1980 | Wednesday | 7.84% |
| 4th | 1980 | Sunday | 7.67% |
| 5th | 2000 | Thursday | 7.65% |
| 6th | 1980 | Tuesday | 7.64% |
| 7th | 2000 | Friday | 7.39% |
| 8th | 2007 | Friday | 7.28% |
| 9th | 2007 | Saturday | 7.01% |
| 10th | 2007 | Sunday | 7.00% |
| 11th | 1980 | Thursday | 6.86% |
| 12th | 2007 | Monday | 6.73% |
| 13th | 2000 | Wednesday | 6.66% |
| 14th | 2000 | Saturday | 6.66% |
| 15th | 1980 | Monday | 6.65% |
| 16th | 1970 | Wednesday | 6.54% |
| 17th | 1970 | Tuesday | 6.34% |
| 18th | 2007 | Thursday | 6.30% |
| 19th | 2000 | Tuesday | 6.03% |
| 20th | 2007 | Tuesday | 6.01% |
| 21st | 2007 | Wednesday | 5.67% |
| 22nd | 1970 | Monday | 5.36% |
| 23rd | 1983 | Tuesday | 5.30% |
| 24th | 1970 | Sunday | 5.04% |
| 25th | 1983 | Wednesday | 5.04% |
| 26th | 1970 | Thursday | 4.98% |
| 27th | 1983 | Monday | 4.33% |
| 28th | 1983 | Thursday | 4.33% |
| 29th | 1986 | Thursday | 4.26% |
| 30th | 2000 | Sunday | 4.25% |
| 31st | 1986 | Wednesday | 4.07% |
| 32nd | 1995 | Monday | 4.04% |
| 33rd | 1995 | Tuesday | 3.79% |
| 34th | 1968 | Friday | 3.73% |
| 35th | 1983 | Sunday | 3.72% |
| 36th | 1969 | Sunday | 3.64% |
| 37th | 1968 | Saturday | 3.47% |
| 38th | 1995 | Sunday | 3.46% |
| 39th | 1986 | Tuesday | 3.11% |
| 40th | 1995 | Wednesday | 3.08% |
| 41st | 1968 | Sunday | 2.89% |

## b.  Winter Peak Loads

The ranking process was repeated for the 350 winter peak loads. After analyzing the ranking it was determined that using the 50 weather years starting on Tuesday and Saturday and the associated 100 winter peak loads (50 years × 2 start days) was representative of the 350 winter peak loads. The top 11 of the 100 peak loads for the Tuesday and Saturday start day sets and the top 37 of the 350 peak loads for the all seven start day sets occurred during the ten most severe winter weather years. For the ten most severe winter weather years, the percentage for the winter peak loads above the average of all 350 winter peak loads averaged 6.86% for Tuesday and Saturday start day sets and 6.23% for all seven start day sets.

The most severe winter weather years are shown in the table below. Note that the winter peak for 1966 of 11.18% above the average of winter peaks from all 50 weather years. This is considerably higher than the 6.20% above the average of annual peaks shown in Table I.8 because the average of annual peak loads for 50 weather years was higher than the average of all 50 winter peak loads.

Table I.11: Most Severe Winter Weather Years (No Day of Week Adjustments)

| Weather Year | Winter Severity Ranking | Deviation From Average of Winter Peak Loads |
| --- | --- | --- |
| 1966 | 1 | 11.18% |
| 2003 | 2 | 10.93% |
| 1985 | 3 | 10.06% |
| 1994 | 4 | 8.44% |
| 1986 | 5 | 7.70% |
| 1982 | 6 | 5.92% |
| 1965 | 7 | 4.45% |
| 2000 | 8 | 3.95% |
| 1977 | 9 | 3.90% |
| 1996 | 10 | 3.51% |

The top 37 of the 350 peak winter loads for the all seven start day sets are shown below.  Note that the 1966 year with a Tuesday start day is the most severe and is over 14% above the average of all 350 peak loads.  This is considerably higher than the 11.18% shown in Table I.11 for the most severe winter weather year because the average of winter peak loads for 50 weather years with no day of week adjustment was higher than the average of all 350 winter peak loads.

Table I.12: Peak Load Variation Details for Winter

| Winter Severity Rank | Winter Severity Year | Start Day for Year | Deviation From Average of All 350 Winter Peak Loads |
| --- | --- | --- | --- |
| 1st | 1966 | Tuesday | 14.31% |
| 2nd | 2003 | Monday | 14.05% |
| 3rd | 1966 | Monday | 13.77% |
| 4th | 2003 | Sunday | 13.51% |
| 5th | 1966 | Wednesday | 13.38% |
| 6th | 2003 | Tuesday | 13.12% |
| 7th | 1966 | Sunday | 12.02% |
| 8th | 2003 | Saturday | 11.76% |
| 9th | 1994 | Saturday | 11.49% |
| 10th | 1985 | Thursday | 11.20% |
| 11th | 1994 | Friday | 10.97% |
| 12th | 1966 | Thursday | 10.92% |
| 13th | 1985 | Friday | 10.86% |
| 14th | 1986 | Thursday | 10.73% |
| 15th | 2003 | Wednesday | 10.66% |
| 16th | 1994 | Sunday | 10.59% |
| 17th | 1985 | Wednesday | 10.32% |
| 18th | 1986 | Wednesday | 10.21% |
| 19th | 1986 | Friday | 9.84% |
| 20th | 1994 | Thursday | 9.26% |
| 21st | 1985 | Saturday | 9.06% |
| 22nd | 1982 | Sunday | 8.90% |
| 23rd | 1985 | Tuesday | 8.62% |
| 24th | 1986 | Tuesday | 8.52% |
| 25th | 1982 | Saturday | 8.39% |
| 26th | 1994 | Monday | 8.18% |
| 27th | 1982 | Monday | 8.02% |
| 28th | 1986 | Saturday | 7.45% |
| 29th | 1965 | Monday | 7.39% |
| 30th | 1965 | Sunday | 6.89% |
| 31st | 2000 | Saturday | 6.88% |
| 32nd | 1977 | Monday | 6.82% |
| 33rd | 1982 | Friday | 6.72% |
| 34th | 1965 | Tuesday | 6.52% |
| 35th | 1996 | Wednesday | 6.42% |
| 36th | 1977 | Sunday | 6.32% |
| 37th | 2000 | Friday | 6.30% |

Since the resulting loads are integrated hourly load shapes, SERVM dynamically calculates ramping requirements to reflect changes in need over the course of the hour in each hour.  In addition to meeting the hourly integrated load, the model must be able to meet the maximum load over the course of the hour which could be several hundred MW greater.  System operation experience has shown variations of this magnitude, and, in actual operation, an hourly purchase must cover the peak of the hour, not just the integrated energy for the hour.

## Unit Specific Adjustments Due to Weather Conditions

Just as the System load responds to weather situations, so do many units on the Southern System.  Specifically, to more accurately capture the capacities of gas and coal units, the model was updated to provide the ability to change the capacities hourly based upon the actual system weighted temperature.  If the temperature is greater than 95°F, most gas units experience a derate in capacity, and when the temperature is less than 95°F, the same units experience an increase in capacity.  For combined cycle units, the capacity is based on temperature and humidity.  Typically, temperatures above 95°F have a decrease in humidity, which leads to a very slight decrease in capacity above 95°F.  Below 95°F combined cycle units experience an increase in capacity similar to CTs.

In addition, some units may have water temperature constraints during the hottest times of drought years and must curtail operation.  This has been primarily a production cost issue, as most of the curtailment occurs in off-peak periods.  Due to system changes caused by the Utility MATS rule, coupled with a review of unit operations, the water temperature constraints are modeled as a 200 MW derate for “once thru” cooling units during the months of July and August during 10 of the hottest drought years.  In the previous study, approximately 627 MW of capacity was modeled as unavailable during July and August for 13 hot and dry years.  The Fleet Operations group was able to proactively manage water temperature issues during the severe drought year of 2007 without derating that much capacity.  The assumptions in this study are consistent with actual operations and result in lower reliability costs than previously assumed.

## Load Forecast Uncertainty

In addition to all variation from normal weather, there remains considerable uncertainty in the load projections for three to four years into the future.  Planning to have a minimum 15.0% reserve margin four years into the future will probably result in a reserve margin either greater than or less than 15.0%.  If load grows more quickly than expected, the reserve margin will be less than 15.0% and the risk of firm load curtailment is greater.  Unexpected strength or weakness in the economy can be a source of load forecast error (LFE).  A structural change in the way electricity is used is also a source of LFE.  Load forecast uncertainty four years into the future (the length of time required to get new CTs on-line) was estimated using 15 years of historical data.  There is a higher probability of over-forecasting the peak than under-forecasting four years out. Southern Company has based its load forecasts on the forecast growth of the economy from Moody’s Analytics and the assumption that there is REDACTED% load growth for 1% real GDP growth. The forecasts in the 16 years from 1993 through 2008 of the real GDP growth for four years into the future were compared with the actual real GDP growth to determine 16 economic forecast errors. The economic forecast errors were multiplied by REDACTED to determine 16 load forecast errors ranging from a maximum under-forecast error of -5.26% to a maximum over-forecast error of 6.50%. Each of the 16 LFEs has a 6.25% (1/16) chance of occurring. By combining and averaging similar LFEs, the 16 LFE points were converted to six LFE points as shown in the following table. For example, points 15 (LFE = 6.48%) and 16 (LFE = 6.50%) were combined and averaged to yield 6.49% and the combined probabilities were summed (0.0625 + 0.0625 = 0.1250).

Table I.13: Load Forecast Error

|  | 16 LFEs |  | 6 LFEs |  |
| --- | --- | --- | --- | --- |
|  | LFE | Probability | LFE | Probability |
| 1 | -5.26% | 0.0625 | -5.26% | 0.0625 |
| 2 | -3.29% | 0.0625 |  |  |
| 3 | -2.51% | 0.0625 |  |  |
| 4 | -2.27% | 0.0625 | -2.69% | 0.1875 |
| 5 | -1.49% | 0.0625 |  |  |
| 6 | -0.84% | 0.0625 |  |  |
| 7 | -0.68% | 0.0625 |  |  |
| 8 | -0.67% | 0.0625 |  |  |
| 9 | -0.58% | 0.0625 | -0.85% | 0.3125 |
| 10 | 0.01% | 0.0625 |  |  |
| 11 | 0.22% | 0.0625 |  |  |
| 12 | 0.56% | 0.0625 | 0.27% | 0.1875 |
| 13 | 1.07% | 0.0625 |  |  |
| 14 | 5.02% | 0.0625 | 3.04% | 0.1250 |
| 15 | 6.48% | 0.0625 |  |  |
| 16 | 6.50% | 0.0625 | 6.49% | 0.1250 |

A graph showing the distribution used for this study and the previous study is included in Figure I.6.  In the previous study, load forecast uncertainty was estimated using 15 years of historical data (load forecasts compared with weather normal load). A biased normal distribution was selected and converted into a discrete distribution, and a set of six ranges was identified which accounted for the entire distribution for the previous study. The graph below shows that while over-forecasting in the current study has a different probability distribution than over-forecasting in the previous study, the under-forecasting probability distribution has changed very little.  Almost all of the EUE cost and reliability and emergency purchase cost results from the under-forecasting cases, so the changes in LFE have very little impact on the results from the current study.  The minimum and maximum values for the distribution used in this study are –5.26 and +6.49 percentage points of the expected value, respectively.  Using this distribution, the EUE across a probability distribution of load forecast uncertainty was estimated.

Figure I.6: Load Forecast Error Distribution Comparison

## Study Year

Target reliability studies should not have the goal of determining the one optimum reserve margin across the next 20 or 30 years.  It is not necessary to select one long-term goal; the system should not be constrained to keep one constant reliability index.  Furthermore, the results of long-term, constant reliability constraints can be clouded by projected changes in load shapes, unit costs, hydro availability, thermal unit availability, and other factors.  The decision at hand is to determine how these constraints affect capacity needs over the next seven years.

For the analyses necessary to determine the incremental change in EUE per additional megawatt of capacity installed, a representative year is selected.  The representative year selected for this study is 2016.

## Capacity Cost

Simple-cycle CT technologies are typically utilized for meeting peaking capacity needs.  Therefore, the cost associated with advancing a CT one year is the cost of capacity used in the analysis.  This cost is also known as the "economic carrying cost" or one-year deferral method.  The CT cost model is a green-field site of four nominal 170 MW units rated at 95°F ambient temperature.  In 2016 dollars, the cost of advancing a CT used in the study was $REDACTED per kilowatt-year.  It includes the following components:

Table I.14: CT Cost Estimations

| CT COST ESTIMATIONS | 2009 Study 2012 Study |
| --- | --- |
| Capital cost of advancing a CT: | $ REDACTED /kW-yr $ REDACTED /kW-yr |
| Plus Fixed Operations and Maintenance, Capital Modifications, and Fuel Inventory Carrying Cost: | + $ REDACTED /kW-yr $ REDACTED /kW-yr |
| Total Cost (2016): | $ REDACTED /kW-yr $ REDACTED /kW-yr |

## Dispatch Order

Every resource that can be called at any time will always be dispatched according to its dispatch price. Nuclear units with the lowest cost are operated at all times. Inexpensive coal (and efficient combined cycles when gas prices are low) will be also run at almost all times. Less efficient gas resources will be called to cycle online for peak hours and will be offline over night and on weekends. Efficient gas CTs are next in the dispatch list followed by older gas units, then oil units. Other resource types such as interruptible customers, pumped storage resources, and emergency hydro capacity have energy limitations and are limited in the dispatch in different ways. Interruptible customers are given shadow prices in the model so that they are only used when prices are relatively high. Pumped storage resources are scheduled based on market price forecasts within the model. Emergency hydro is only called when all other resources are unavailable. The logic for all types of energy limited resources works to conserve capacity for peak periods while also attempting to maximize energy value.

## Cost of Expected Unserved Energy

The cost of EUE has been one of the most uncertain of all the assumptions made in the Reserve Margin study.  The model allocates a portion of the costs to different customer classes for appropriate durations in order to appropriately match the expected costs of EUE.  In addition, if a customer is curtailed in one hour and load is returned to the customer in the following hour, additional load will be added to account for those customers’ appliances being in start-up.

To estimate this cost or value, an outage cost survey of GPC and Mississippi Power Company customers was conducted in 2011 by Freeman Sullivan & Company.  This survey was conducted among the following four customer classes:

Residential;

Commercial (below 1 MW average demand);

Industrial (below 1 MW average demand); and

Large business (commercial and industrial customers above 1 MW average demand).

- The cost of EUE for these four customer classes is shown in the following table.

Table I.15: EUE Cost

| EUE Cost in 2012 $ |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Outage Scenario | Residential ($/kWh) | Commercial ($/kWh) | Industrial ($/kWh) | Large Business ($/kWh) | Weighted Average ($/kWh) |
| 1 hour, no warning, summer | $REDACTED | $REDACTED | $REDACTED | $REDACTED | $REDACTED |
| % | REDACTED% | REDACTED% | REDACTED% | REDACTED% |  |
| Contribution to Weighted Average | $REDACTED | $REDACTED | $REDACTED | $REDACTED |  |

GPC determined what percentages each customer segment contributes to a generic block of load that would be shed in such times of need.  Then, the cost of EUE was adjusted by the weight each customer class would contribute in such a load-shed scenario.  The cost of EUE (in 2012 dollars) was determined in the previous study to be $REDACTED per kilowatt-hour. The increase to $REDACTED per kilowatt-hour is driven by the higher costs for commercial and industrial customers as shown in the following table.

Table I.16: EUE Cost Comparison

| EUE Cost for 1 hour outage | New Study | Previous Study |
| --- | --- | --- |
| Residential | REDACTED | REDACTED |
| Commercial (C) | REDACTED | REDACTED |
| Industrial (I) | REDACTED | REDACTED |
| Large Business C | REDACTED | REDACTED |
| Large Business I | REDACTED | REDACTED |

The higher cost for commercial and industrial customers is driven by increased computerization and by a difference in methodology for excluding outliers. For the new study, the top 0.5% of values normalized by usage was dropped from the analysis for the residential, commercial and industrial segments, which is the current standard practice for this type of survey.  For the previous study which was based on a survey conducted in 1990, the values that exceeded the estimated cost associated with the installation of backup generation or uninterruptible  power supply (UPS) to avoid a given outage scenario were dropped from the analysis for the residential, commercial and industrial segments. The approach utilized in the latest study includes more high cost responses and is more appropriate because expecting customers to provide back-up generation is unreasonable as backup power's costs and frequency of use are very uncertain. The cost of EUE (in 2016 dollars) for the new study was determined to be $REDACTED /kWh.

## Planned Outage Patterns

Planned outages occur most often in the shoulder months because the demand on the units to be run during the peak demand months does not allow for a lot of down time.  For Southern Company, no planned maintenance events are scheduled for summer months except for summer period maintenance outages that are modeled for the oil CTs located in ozone non-attainment areas to prevent SERVM from committing them during the summer months.  Maintenance outages are added by SERVM during low demand periods such that the region’s maintenance outage rate achieves the historical rate for that region.  For Southern Company, the 2016 scheduled maintenance outages are incorporated into the model with additional maintenance outages added during periods of low demand such that the overall maintenance outage rate for Southern Company achieves the 2016 projected maintenance outage rate.

REDACTED

Figure I.7: Planned Outages

# II. SIMULATION PROCEDURE

## SERVM Case Specification

The simulations were designed to estimate System generation reliability across a range of weather conditions, load forecast errors (LFEs), and reserve margins.  Seven discrete reserve margin levels were simulated to calculate the expected reliability costs over a broad range of scenarios.  Fifty specific weather years each with Tuesday and Saturday start days were run in combination with varying LFEs.  Weather years were paired such that loads and hydro scenarios were matched.  The simulation variables were as depicted in Table II.1:

Table II.1: SERVM Case Variables

| Weather and Hydro Years |  | Reserve Margins |
| --- | --- | --- |
| 1962 | 1987 | 10% |
| 1963 | 1988 | 12% |
| 1964 | 1989 | 14% |
| 1965 | 1990 | 15% |
| 1966 | 1991 | 16% |
| 1967 | 1992 | 18% |
| 1968 | 1993 | 20% |
| 1969 | 1994 |  |
| 1970 | 1995 |  |
| 1971 | 1996 |  |
| 1972 | 1997 |  |
| 1973 | 1998 |  |
| 1974 | 1999 |  |
| 1975 | 2000 |  |
| 1976 | 2001 |  |
| 1977 | 2002 |  |
| 1978 | 2003 |  |
| 1979 | 2004 |  |
| 1980 | 2005 |  |
| 1981 | 2006 |  |
| 1982 | 2007 |  |
| 1983 | 2008 |  |
| 1984 | 2009 |  |
| 1985 | 2010 |  |
| 1986 | 2011 |  |

Without accounting for load forecast uncertainty, the total number of combinations for the analysis would be 50 × 2 × 7, or 700 cases.  Taking into account the six load forecast points yields 4200 cases (50 × 2 × 7 × 6 cases).  Estimating EUE for each of the 4200 cases through a rigorous application of SERVM provides sufficient data for regression analysis of other combinations not specifically calculated in the detailed models.

Table II.2 lists the EUE for the 10 highest weather/hydro datasets after emergency purchases are applied.  From the Table, for example, at 10% reserves, with a hot and relatively dry weather dataset (#4), and 2.69% LFE, the EUE is 1,450 megawatt-hours.  This could be interpreted as dropping roughly 150 MW of load for ten hours or some other combination that equals ~1500 megawatt-hours.

Table II.2: Annual EUE with 2.69% LFE

| Weather/ Hydro Data Set | Annual EUE (MWh) with 2.69% LFE by Reserve Margin |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10% | 12% | 14% | 15% | 16% | 18% | 20% |
| 1 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 2 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 3 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 4 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 5 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 6 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 7 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 8 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 9 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |
| 10 | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED | REDACTED |

## Probabilities of Occurrence for Input Variables

As has been discussed in the previous sections, the chronological variable inputs into the model, excluding the unit outage data, are used to represent appropriate ranges of data.  For example, the weather years selected to exemplify load variations due to temperature changes represent 50 years of historical data.  This is also true for the hydro patterns developed.  The implementation of load forecast uncertainty into the evaluation is representative of the potential (supported by historical information) load forecasting errors when looking out into the future.  Using probabilistic evaluation techniques requires each of these variables to have a designated probability of occurrence.  Table II.3 depicts the probabilities assigned to each weather/hydro year and each load forecast uncertainty.  A total probability associated with a combination of these variables can be calculated using the associated probabilities.

Table II.3: Input Variable Probabilities

| LFE | LFE Probability | Weather/Hydro Probability | LFE Probability times Weather/Hydro Probability | Weather/Hydro Years | Total Probability |
| --- | --- | --- | --- | --- | --- |
| -5.26% | 0.0625 | 0.02 | 0.00125 | 50 | 0.0625 |
| -2.69% | 0.1875 | 0.02 | 0.00375 | 50 | 0.1875 |
| -0.85% | 0.3125 | 0.02 | 0.00625 | 50 | 0.3125 |
| 0.27% | 0.1875 | 0.02 | 0.00375 | 50 | 0.1875 |
| 3.04% | 0.1250 | 0.02 | 0.00250 | 50 | 0.125 |
| 6.49% | 0.1250 | 0.02 | 0.00250 | 50 | 0.125 |
| Total |  |  |  |  | 1 |

As shown, the probabilities assigned for the weather years are equal.  Since each LFE is simulated through 50 weather years, the total product sums to 1.00 or 100%.

## Reliability Model Simulations

Generation reliability simulations are conducted using a model that incorporates Monte Carlo techniques.  Monte Carlo analysis uses a random number generator to determine generating unit availability for the System.  For each iteration, the model simulations will randomly select the state of a generating unit as fully operational, partially failed, or completely failed and determine if the system experiences loss of load and associated EUE.  Historical information concerning load forecast uncertainty, weather, and hydro energy is used to construct numerous cases that could occur for a future year.

For a single reserve margin, a set of 600 cases were developed using the following table:

Table II.4: Cases for Specific Reserve Margin

| Weather Years | Start Days | Load Forecast Error Points | Total Number of Cases Modeled |
| --- | --- | --- | --- |
| 50 | 2 | 6 | 600 |

In previous studies, for each of the cases, each hour of the year was modeled with 400 iterative draws from the distribution of generating unit outage and duration data to determine if there exists a deficiency of generating capacity to meet load demand.  However, statistical analysis performed indicates that the actual mean value of EUE +/-2.5% can be calculated at a 95% confidence interval by using 50 draws.  A deficiency of generating capacity in a given hour is recorded as a loss of load hour.  The magnitude of the outage during that hour is measured by EUE.  Based upon the model simulations, average reliability purchases, emergency purchases, and EUE are determined for each case across all hours in the month.  Then, the average reliability purchases, emergency purchases, and EUE in each case are multiplied by the probability of occurrence for that case and the result for all cases is summed to determine an expected value of reliability purchases, emergency purchases, and EUE for the study year.  Figure II.1 shows the formula used for calculating EUE, and Table II.5 provides an example of implementing the formula for a sample data set.  Table II.6 similarly illustrates an example of purchases for the study year.

Figure II.1: Variable Calculation Formula

600

Expected Y =      (Y i  x  Probability i )

i=1

where,  Y = EUE and, i = number of cases

Table II.5: Sample Calculation of EUE at 10% Reserves

| SAMPLE CALCULATION OF EUE AT 10% RESERVES |  |  |  |  |
| --- | --- | --- | --- | --- |
| Weather/ Hydro Data Set | LFE | EUE (MWh) | Probability | Weighted EUE (MWh) |
| 1 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 2 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 3 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 4 | 2.69% | REDACTED | 0.001875 | REDACTED |
| 5 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 6 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 7 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 8 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 9 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 10 | 5.26% | REDACTED | 0.000625 | REDACTED |
| Total EUE (MWh) at 10% Reserves: |  |  |  | REDACTED |

Table II.6: Sample Calculation of Purchases at 10% Reserves

| SAMPLE CALCULATION OF PURCHASES AT 10% RESERVES |  |  |  |  |
| --- | --- | --- | --- | --- |
| Weather/ Hydro Data Set | LFE | Purchases (MWh) | Probability | Weighted Purchases (MWh) |
| 1 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 2 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 3 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 4 | 2.69% | REDACTED | 0.001875 | REDACTED |
| 5 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 6 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 7 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 8 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 9 | 5.26% | REDACTED | 0.000625 | REDACTED |
| 10 | 5.26% | REDACTED | 0.000625 | REDACTED |
| Total Weighted Purchases (MWh) at 10% Reserves: |  |  |  | REDACTED |

An expected value of EUE, reliability purchases, and emergency purchases was calculated for all seven reserve margin points.  By applying regression analysis to the expected values, a curve summarizing EUE cost, reliability and emergency purchase cost, and expected capacity cost as a function of reserve margin was developed.  These results are discussed in detail in the following section.

# III. BASE CASE RESULTS

In theory, the optimum reserve margin should be the reserve margin that results in the minimum total system costs. Since the production and capacity costs for all base load resources and other resources do not change as reserve margin varies, they are excluded. The three cost components that do vary from each reserve margin level were added together to create an aggregate system cost curve. The minimum point on the resultant curve, which is at approximately 14% reserve margin, represents the economically optimum reserve margin.  This graph is presented below.

Figure III.1: Optimum System Planning Reserve Margin

REDACTED

## Key Drivers

The optimum reserve margin chart above demonstrates nearly $50M per year of reliability costs at a 20% reserve margin. Based on recent history, this projection seems too high. However, the model is setup to simulate what risks could materialize in the period from 2016 - 2021. The assumptions made for this timeframe reflect a number of changes that are expected to take place in the next several years. Regional reserves should come down as load grows, units retire, and fewer new units are added. The implications of the assumptions used in the model for the study period are discussed in the following sections.

In addition, it is important to recognize that SERVM is an hourly model, so all costs consist of hourly purchases and hourly production costs above that of a marginal CT. In actual practice, the reliability costs may be managed on a weekly, monthly, or even annual basis. If there is significant unplanned load growth inside the four-year planning window, annual reliability purchases may be made to bring reserves back closer to target, or seasonal purchases during particular months may be made to reduce risk. Such purchases were made in the 1999 - 2001 timeframe. Those years were marked by higher load growth than expected and relatively low regional reserves. Cases were run in SERVM with similar conditions to ensure that the model's predictions reasonably matched the cost of the purchases from history. Use of historical market data to calibrate SERVM purchases provided comfort that the model would adequately capture the scarcity premiums in the market regardless of how those purchases might be executed in actual practice.

## Regional Capacity

Resource adequacy planning requires modelers to build assumptions about the level of support available from neighboring regions. Merchant capacity has been present in the southeastern US for over 15 years, but the sporadic nature of its availability requires planners to be conservative in assumptions about its presence in the future. Merchant capacity may be bought by other load serving entities in the region or may not have firm transmission. For these reasons, merchant capacity was not assumed to be present in the base case simulations. In addition, neighboring utilities were projected to be at their target reserve margins of 15% to 20%. While Southern recognizes that most utilities will have more capacity than this over the next few years, prudency dictates not relying on this capacity. A sensitivity was performed to assess the optimum economic reserve margin if regional reserves are consistently high. The results of that sensitivity are discussed in subsequent sections.

## Weather Diversity

While SERVM assumes that capacity will be available from neighboring utilities, it is not because Southern is relying on other utilities to carry extra capacity for Southern's benefit. The reason that Southern is expected to be able to buy power is that neighbors do not typically peak in the same hour as Southern does. In the summer, Southern can see average diversity of 3-5% with its neighbors which results in substantial available capacity. A sensitivity was performed to isolate this weather diversity benefit.

## Load Growth Uncertainty

In the past 10 years, almost all of the economic load uncertainty has been negative. Loads have always grown slower than expected or have actually shrunk. Southern Company believes this to be cyclical in nature and that periods of higher load growth than expected are possible similar to what occurred in the late 1990s. Without this potential for faster than expected load growth, the optimum economic reserve margin would be lower.

## Market Clearing

Scarcity pricing is driven by a number of complex factors. While Southern Company has calibrated SERVM's scarcity pricing logic to historical scarcity market prices, those relationships may not always hold. During scarcity situations, Southern Company will be subject to the market and because of the importance of service reliability should be expected to make purchases even at prices well above $1,000/MWh if they are reliably available. A sensitivity was performed to assess the impact that market price uncertainty could have on the target reserve margin.

## Unit Performance

Southern Company has an excellent track record of unit performance in recent history. The average on peak EFOR for the past 5 years for the fleet is only 1.7%. If units do not perform as well as they have historically, the target reserve margin would need to move up. A sensitivity on system EFOR was also performed.

## Risk Analysis

The comparison of average reliability costs to average CT carrying costs results in minimum system costs at a 14% reserve margin. However, since reliability costs are highly dependent on the selected scenario, the comparison is not completely valid. The following figure illustrates the volatility in market purchases and EUE cost exposure. In scenarios in which load grows faster than expected, temperatures are higher than expected, or unit performance is poorer than expected, the exposure can be much higher than average.

Figure III.2: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets

REDACTED

Zooming in on the most extreme cases for each reserve margin further highlights the risk in carrying low reserves. The following figure shows the exposure for the top 10% of all cases as ranked by market purchases and EUE cost exposure. The most extreme case simulated at a 10% reserve margin shows over $5 billion in total exposure, while the most extreme case at a 15% reserve margin is approximately $1.5 billion.

Figure III.3: Market Purchases and EUE Cost Exposure Under Different Reserve Margin Targets:       Top 10%

REDACTED

To make a more appropriate comparison between volatile reliability costs and fixed capacity costs, several steps can be taken.  In the casualty insurance business, customers have the option of paying an insurance premium to cover the impact of a catastrophic loss.  In that example, the annual insurance premium is higher than the cost of the loss times its probability.  Customers and regulators are comfortable with paying an amount greater than the average loss because it makes the payments fixed.  In the same way, the prudent course of action for utilities is to procure capacity at fixed rates slightly above the optimum reserve margin to prevent high cost outcomes.

The table below illustrates the Value at Risk at various confidence levels for a range of reserve margin targets.  Below the minimum cost reserve margin, total system costs drop as capacity is added.  At levels slightly above the minimum cost reserve margin, total system costs increase slightly as capacity is added.  In this range of 14% to 16%, the additional average cost is minimal but the risk benefits are substantial.  Moving from a 14% reserve margin to a 15% reserve margin reduces the additional exposure above the average exposure by $17M at an 85% confidence while only increasing the average cost by $2M.

Table III.1: Value At Risk

| Reserve Margin | Weighted Average System Costs ($M) | VaR 80 ($M) | VaR 85 ($M) | VaR 90 ($M) | VaR 95 ($M) |
| --- | --- | --- | --- | --- | --- |
| 10% | 346 | 171 | 255 | 410 | 712 |
| 12% | 307 | 111 | 152 | 246 | 489 |
| 14% | 293 | 69 | 117 | 182 | 335 |
| 15% | 295 | 59 | 100 | 164 | 294 |
| 16% | 300 | 49 | 91 | 146 | 250 |
| 18% | 321 | 40 | 61 | 111 | 176 |
| 20% | 351 | 28 | 49 | 84 | 153 |

## Reliability Metrics

The incremental annual capacity carrying cost at any given reserve margin is determined by multiplying the incremental capacity (kW) by the economic carrying cost of $REDACTED/kW-year.  This is represented in Figure III.4 by a straight line with a positive slope when graphed as a function of reserve margin.

Figure III.4: Capacity Cost

REDACTED

The cost of EUE at each reserve margin is determined by multiplying the amounts of EUE at each reserve level created in the analysis (Figure III.5) by the assumed cost of EUE.  Figure III.6 illustrates EUE cost as a function of reserve margin.

Figure III.5: Expected Unserved Energy

REDACTED

Resource adequacy assessments in other regions typically use Loss of Load Expectation (LOLE) as the primary metric of reliability. LOLE is a count of the number of days in a given study year in which the system experienced any firm load shed. This metric does not measure the magnitude of the event and is relatively sensitive to a number of input assumptions. The typical LOLE standard is one day in 10 years as a minimum level of reliability. For comparison purposes, the following figure illustrates how Southern's selected target reserve margin is substantially higher than this standard.

Figure III.6: Loss of Load Equivalent

REDACTED

Figure III.7: Expected Unserved Energy Cost

REDACTED

Reliability purchase and emergency purchase costs are estimated by multiplying reliability purchase energy and emergency purchase energy, respectively, by the assumed purchased energy price.  Due to the insignificant amount of emergency purchases, reliability and emergency purchases are combined in the following figures.

Figure III.8: Purchase Energy

REDACTED

Figure III.9: Purchase Energy Cost

REDACTED

The implied theory is that EUE, emergency purchases, and reliability purchases are becoming more likely as reserve margin is reduced.  Consequently, their costs increase as the reserve margin gets lower.

# IV.  SENSITIVITY ANALYSIS

The basis for the data for unit performance, weather, load forecast error, hydro availability, market prices and other inputs is from historical information.  Other data such as market availability is based on forecasted information.  While the broad range of scenarios capture extreme events and market prices, there remains risk that conditions could occur in the future that extend beyond the range of what is contemplated in the base case model.  Some examples are higher unit outages, higher market prices, and less merchant capacity than expected.  Each of these scenarios was modeled to examine the impact on the optimum reserve margin.

## 50% Higher EFOR

Unit outages were increased by 50% and simulations were performed across all combinations of weather with a Saturday start day and load forecast error for 50 iterations.  The results of the 50% higher unit outage scenario showed that total reliability costs were approximately 12% higher in the 15% reserve margin level case and the optimum reserve margin moved from 14% to 15%. With new environmental controls being added and the fleet of resources aging, it is possible that the System forced outages rates could increase by amounts similar to these scenarios.

## No Weather Diversity

Neighboring utilities were forced to peak at the same hour as Southern eliminating some excess capacity that Southern could purchase.  Simulations were performed across all combinations of weather with a Saturday start day and load forecast error for 50 iterations.  The results of the no weather diversity scenario showed that total reliability costs were approximately 78% higher in the 15% reserve margin level case and the optimum reserve margin moved from 14% to 18.5%.  While this case is not realistic, it illustrates the benefit that Southern receives by participating in a dynamic energy market.

## 50% Reduced Transmission

Transmission capabilities with neighboring utilities were reduced by 50% and simulations were performed across all combinations of weather with a Saturday start day and load forecast error for 50 iterations.  The results of the 50% reduced transmission scenario showed that total reliability costs were approximately 4% higher in the 15% reserve margin level case and the optimum reserve margin moved from 14% to 14.5%.  Since the optimum reserve margin only moved slightly, transmission capability appears to be adequate from a reliability standpoint.

## Capacity Cost Sensitivity

The carrying cost of capacity directly affects the optimum economic reserve margin. With high carrying costs, the economic optimum reserve margin is lower than the base case. With low carrying costs, the optimum reserve margin is higher than the base case., Determination of the optimum reserve margin with different capacity costs did not require running any simulations.  As seen in Figure IV.1, reserve margin decreases as capacity cost increases.

Figure IV.1: Reserve Margin as a Function of Capacity Cost

REDACTED

## 50% Reduced Market Price

Scarcity prices were reduced by 50% (scarcity prices are premiums above the dispatch cost of the marginal resource) and simulations were performed across all combinations of weather with a Saturday start day and six load forecast errors for 50 iterations.  The results of the reduced market price scenario showed that total reliability costs were 14.6% lower than in the 15% reserve margin level case and the optimum reserve margin went from 14% to 12.75%.  Given that market purchase costs for the base case were calibrated to actual history, such low market prices are not expected.

## Higher Regional Reserves

The reserves of neighboring utilities or regional reserves were increased by 5% and simulations were performed across all combinations of weather with a Saturday start day and 6 load forecast errors for 50 iterations.  The results of the increased regional reserves scenario showed that total reliability costs were approximately 13% lower in the 15% reserve margin level case and the optimum reserve margin moved from 14% to 12%.

## Short Term Load Forecast Error

Short term load forecast errors were used and simulations were performed across all combinations of weather with a Saturday start day and load forecast error for 50 iterations.  The results of the short term load forecast error scenario showed that total reliability costs were approximately 11% lower in the 15% reserve margin level case and the optimum reserve margin decreased from 14% to 13%. The short term load forecast errors used are in the table below.

Table IV.1: Short Term Load Forecast Error

| Short Term Load Forecast Error |  |
| --- | --- |
| LFE | Probability |
| -2.20% | 0.04856 |
| -1.49% | 0.1667 |
| -0.75% | 0.2778 |
| 0.10% | 0.2222 |
| 1.64% | 0.1667 |
| 4.32% | 0.1111 |

# V.  CONCLUSION

## Optimum System Planning Reserve Margin

Based on economic reliability analysis and current system conditions, as well as incorporating some of the possible sensitivity impacts of forced outages, market prices, EUE cost, and neighbor available capacity, the minimum cost point on the reliability cost graph is approximately 14%.  Since capacity cost is fixed once contracted, reliability costs can vary widely, and some unknown risks are likely not captured in this analysis, a slightly higher target reserve margin of 15% was selected.  This reserve margin represents only a slightly higher cost than the minimum cost point and substantially higher confidence of lower reliability costs.  Therefore, it is recommended that the system maintain a 15% target system planning reserve margin for three-years out (beginning 2016), and inside the three-year window, maintain a minimum system reserve margin of 13.5%. These recommendations are designed to provide guidance for resource planning decisions but should not be considered absolute targets. The large size of capacity additions, the availability and price of market capacity, or economic and political changes may justify decisions that result in reserve margins above or below the targets.

Figure V.1: Optimum System Planning Reserve Margin

REDACTED

Generating Capacity = $REDACTED/kW, EUE = $REDACTED/kWh

Figure IV.2 shows how each of the primary components (weather, market risk, unit performance, and load-forecast error) contributes to the overall required System planning reserve margin.

Figure V.2: Economic Components of Reserve Margin

REDACTED%

REDACTED%

REDACTED%

REDACTED%

The 15% target system planning reserve margin recommended for the System reflects the results of the economic study and a variety of other information available and is extremely important in planning to best meet customer needs.

# VI. SUMMARY

After an analysis of the current and near-term projected generation reliability state of the Southern electric system, it is concluded that the system should maintain a 15% system planning reserve margin target three years out and inside the three-year window should maintain a 13.5% minimum system planning reserve margin.  There are three significant updates to the analysis from the previous study that contributed to this result:

- Incremental capacity has significant benefits beyond avoiding firm load shed events. Previous market modeling did not fully capture the benefit provided by incremental capacity because it did not model the unique units and loads for each neighboring region. The enhanced version of SERVM used in this study utilizes distinct load shapes and the actual units for each region to accurately capture the frequency and price of purchases all the way from the cost of a marginal CT to just before shedding firm load. This enhancement resulted in a higher total purchase power cost and a slightly higher reserve margin for the minimum cost point as a base case.

- Previous reserve margin studies have utilized conservative regional reserve margin forecasts for use in market modeling. Even with conservative forecasts of regional reserves, the modeled market in the previous study had excess capacity beyond what would normally be available.  This study utilizes the target reserve margin for each region and assumes zero merchant capacity since the study's recommendations will apply for a number of years. The effect of this assumption change resulted in a slightly higher reserve margin for the minimum cost point. However, the study also recognizes that individual resource decisions should consider the actual price and availability of capacity in the market and may result in a higher or lower reserve margin than targeted.

- The cost of EUE is substantially higher than in previous studies. Since EUE is so infrequent even at lower reserve margins, this change only slightly increased the reserve margin for the minimum cost point.

Industry experience, system operations input, perceptions of acceptable risks, and an understanding of the strengths and weaknesses of the mathematical models were all considered in determining the optimum reserve margin level for the Southern Electric System in the next 7 years.