## Residential
[13 empty] | PUBLIC DISCLOSURE | [13 empty] | PUBLIC DISCLOSURE | [9 empty] | PUBLIC DISCLOSURE
Georgia Power Company - 2013 IRP DSM - Technology Catalog - Residential | [13 empty] | Georgia Power Company - 2013 IRP DSM - Technology Catalog - Residential | [13 empty] | Georgia Power Company - 2013 IRP DSM - Technology Catalog - Residential
Measure Details |  | Description | Measure Categorization | Qualitative Screening | [9 empty] | Economic Tests |  |  |  |  | Energy/Demand Impacts | [5 empty] | Cost Impacts |  |  | Additional Measure Data
ID Number | DSM Measure Name | General Description | End-Use Category | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Pass to Economic Screen | Notes | TRC | RIM | PCT | SCT | Pass TRC? | Energy (kWh) savings (1) | Peak Coinc. Demand (kW) savings (1) | Savings Reference | Savings/ Modeling/Cost Notes | Modeled Facility Type | Applicable Facilities | Incremental Measure Cost | Cost Reference | Utility Avoided Cost (Lifetime) | Measure Life | Meas. Life Reference | Levelized cost per lifetime kWh | Size of eligible market(2) | Achievable Mkt Pen-Agg (3) | Current Saturation | Saturation Reference | Non-electric part. Benefits - gas (therms) | Non-electric part. Benefits - water (gal) | TEAPOT Ramp Rate
|  |  |  | Difficult to Quantify Savings | Current Practice | Better Measure Available | Immature or Unproven Technology | Limited Applicability | Poor Customer Acceptance | Health & Environ. Concerns | End-Use Service Degradation | [25 empty] | TEAPOT Ramp Rate
1 | Clothes Dryer - Heat Pump | equipment replacement | Elec. Clothes Dryer | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
2 | Clothes Dryer - Microwave | equipment replacement | Elec. Clothes Dryer | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
3 | Clothes Dryer - Moisture Sensor | most, if not all, dryers now have moisture sensors built in. ENERGY STAR does not rate dryers - their website states that "ENERGY STAR does not label clothes dryers since there is little difference in the energy use between models." | Elec. Clothes Dryer | [8 empty] | No | Standard practice for new dryers | bar: Qualitative Screening 1 to Qualitative Screening 2
4 | Clothes Washer - Energy Star | this unit uses 50% less energy than standard | Washing Machine | [8 empty] | Yes |  | 5.2324 | 0.61147 | 6.6392 | 5.3105 | YES | 826.53 | -0.0018706 | GPC EnerSim model | 1 unit, elec WH | SF | SF, MF, MH | 214 | RSMeans Change: Washing machine, energy star, front loading, minimum. | 1119.7421 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 10446.535 | LO_Medium
5 | Clothes Washer - CEE Tier 2 or Tier 3 | higher efficiency standards than ES | Washing Machine | [8 empty] | No | Same as ID# 4 - Clothes Washer - Energy Star
6 | Dishwasher - Energy Star | this unit uses 25% less energy than standard | Dishwasher | [8 empty] | No | standard practice for new dishwashers | bar: Qualitative Screening 2
7 | Cooktop - High-Efficiency Induction |  | Cooking | [8 empty] | Yes |  | 0.030463 | 0.69675 | 0.043721 | 0.031475 | NO
8 | Oven - High-Efficiency Convection | Heated air is continuously circulated around the food being cooked for more even heat distribution. Temp and cooking times will decrease. On avg, the use of a convection oven will save about a third on energy use. | Cooking | [8 empty] | Yes |  | 0.04226 | 0.72213 | 0.058522 | 0.043622 | NO
9 | High Eff. Refrigerator - Energy Star | (from EnergyStar website) this unit uses 15% less energy than standard | Refrigerator 1, Refrigerator 2 | [8 empty] | Yes |  | 1.4924 | 0.60436 | 2.4693 | 1.5441 | YES | 165.49 | 0.016791 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 81 | RSMeans Change: Refrigerator, energy star qualified, 18 CF max avg. | 120.8829 | 14 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
10 | Energy Star Compact Refrigerator (<7.75 cu. ft.) | this unit uses 20% less energy than standard | Refrigerator 1, Refrigerator 2 | [8 empty] | Yes |  | 1.5929 | 0.53597 | 2.972 | 1.6508 | YES | 77.39 | 0.0058701 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 23 | For change, Avg of top 10 energy star compact refrigerators <7.5 cu ft http://www.ajmadison.com/b.php/Compact%3B%24100+-+%24199%2C%24200+-+%24299%2C%24300+-+%24399%2C%24500+-+%24599%2C%24600+-+%24699%2C%24700+-+%24799%2C%24900+-+%24999%3BEnergy+Star+Rated%3BRefrigerators/Nf~_total_capacity%7CBTWN%203%207.5%3BNs~_all_top_seller_position_%7C0%3BN~26+4294960671+4294966140+10+11+4+13+14+15+17%3Bpropname_total_capacity~Total%20Capacity | 36.6373 | 9 | http://log-homes.thefuntimesguide.com/2007/03/life_expectancy_of_homes.php | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
11 | Efficient Refrigerator O&M | includes turning off anti-sweat heater, keep refrig b/w 35-38 F, placement (keep coils away from wall), not having ice-maker, coil cleaning and replacement | Refrigerator 1, Refrigerator 2 | [8 empty] | Yes |  | 0.28565 | 0.4656 | 0.6135 | 0.29684 | NO
12 | Refrigerator/Freezer Recycling | remove working refrigerator rather than it being stored/used in garage or basement | Refrigerator 1, Refrigerator 2 | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 999.99 | 0.48455 | 999.99 | 999.99 | YES | 757.17 | 0.0611 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 0 | No equipment cost. | 286.4702 | 8 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
13 | High efficiency Freezer (10% above std.) - Energy Star | this unit uses 10% less energy than standard | Freezer | [8 empty] | Yes |  | 2.4341 | 0.58175 | 4.1841 | 2.5228 | YES | 138.6 | 0.017603 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 32 | Change: Average of 4 Energy Star freezers above 20 Cu.Ft. looked up at Home Depot. http://www.homedepot.com/Energy-Star/h_d1/N-5yc1vZ1z141o3/Ntk-All/Ntt-Freezer/h_d2/Navigation?langId=-1&storeId=10051&Ntx=mode+matchall&catalogId=10053&Nu=P_PARENT_ID&searchNav=true | 77.8915 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
14 | Energy Star Compact Freezer (<7.75 cu. ft) | this unit uses 20% less energy than standard | Freezer | [8 empty] | Yes |  | 0.17011 | 0.53875 | 0.31576 | 0.17643 | NO
15 | Energy Star Computer (desktop or laptop) | in sleep mode, uses 4 watts or less | Other | [8 empty] | No | Standard practice for new computers | bar: Qualitative Screening 2
16 | Energy Star Monitor | In sleep mode, uses 2 watts or less. In off mode, uses 1 watt or less | Other | [8 empty] | No | Energy Star current practice on all models | bar: Qualitative Screening 2
17 | Energy Star Copier & Fax Machine (imaging equipment) | sleep or power down when not in use, and use 25% less electricity compared to standard models when on | Other | [8 empty] | No | Same as 'Energy Star Multifunction Device' (Combined with other measures into #163)
18 | Energy Star External Power Adapter | On average, 30 percent more efficient than conventional models | Other | [8 empty] | No | Energy Star external power adapter program still being developed | bar: Qualitative Screening 1; Qualitative Screening 4
19 | Energy Star Multifunction Device | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Other | [8 empty] | No | Currently only 47% of new MFDs are Energy Star certified (http://www.energystar.gov/ia/partners/prod_development/revisions/downloads/img_equip/ES_Imaging_Equipment_Kickoff_Webinar_Presentation.pdf) (Combined with other measures into #163)
20 | Energy Star Printer | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Other | [8 empty] | No | Currently only 67% of new printers are Energy Star certified (http://www.energystar.gov/ia/partners/prod_development/revisions/downloads/img_equip/ES_Imaging_Equipment_Kickoff_Webinar_Presentation.pdf) (Combined with other measures into #163)
21 | Energy Star Scanner | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Other | [8 empty] | No | Limited applicability, more common device is MFD that includes scanner. (Combined with other measures into #163) | bar: Qualitative Screening 3; Qualitative Screening 5
22 | Energy Star Cordless Phones | perform much more efficiently than conventional units and use about one-third of the energy | Other | [8 empty] | Yes |  | 0.99979 | 0.48718 | 2.0522 | 1.0381 | NO
23 | Energy Star DVD | When off, use as little as one quarter of the energy used by standard models | Other | [8 empty] | Yes |  | 0.34891 | 0.48246 | 0.72319 | 0.36228 | NO
24 | Energy Star TV | this unit uses 25% less energy than standard | Color TV | [8 empty] | No | standard practice for TVs | bar: Qualitative Screening 1 to Qualitative Screening 2
25 | Energy Star Combination Units (TV/VCR, TV/DVD) | use about 35% less energy than standard units | Color TV | [8 empty] | No | standard practice | bar: Qualitative Screening 1 to Qualitative Screening 2
26 | Energy Star VCR | VCRs use 30% less energy than standard | Other | [8 empty] | No | Limited applicability | bar: Qualitative Screening 1 to Qualitative Screening 2
27 | Energy Star Set-Top Boxes | Includes cable boxes, satellite receivers, Internet access devices, and video game consoles | Other | [8 empty] | Yes |  | 0.64346 | 0.69589 | 0.92466 | 0.66234 | NO
28 | Energy Star Home Audio | When they're off, ENERGY STAR qualified audio products use as little as one tenth of the energy used by standard models | Other | [8 empty] | Yes |  | 0.53651 | 0.45671 | 1.1747 | 0.56041 | NO
29 | Energy Star Battery Charging System | On average, use 35% less energy than conventional models | Other | [8 empty] | Yes |  | 0.61145 | 0.48286 | 1.2663 | 0.6349 | NO
30 | Energy Star Digital to Analog Converter Box | consume less than 8 watts when on, 4 watts in sleep and 1 watt when off - automatically power down after 4 hrs of inactivity | Other | [8 empty] | No | No longer supported by Energy Star | bar: Qualitative Screening 5; Qualitative Screening 8
31 | Smart strip surge protector | stop or reduce idle current draw when electronics are not in use | Other | [8 empty] | Yes |  | 0.67854 | 0.46726 | 1.4522 | 0.7062 | NO
32 | ENERGY STAR HOME/ EarthCents Home | at least 15% more energy efficient than homes built to the 2004 International Residential Code | **WHOLE HOME** | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 1.4574 | 0.75492 | 1.9305 | 1.506 | YES | 2178.93 | 0.27121 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 1500 | Used cost from typical earthcents home | 2186.0661 | 20 | GPC Earthcents program | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
33 | New Home - 30% above code |  | **WHOLE HOME** | [8 empty] | Yes |  | 0.45459 | 0.73557 | 0.59885 | 0.46823 | NO
34 | New Home - 50% above code |  | **WHOLE HOME** | [8 empty] | Yes |  | 0.47247 | 0.72159 | 0.64148 | 0.48733 | NO
35 | Dual Fuel (Add-On) Heat Pump Package System Energy Star | assume this involves adding heat pump to existing furnace, which will be used as back-up heat. | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | No | Most residential units are split systems. | bar: Qualitative Screening 4 to Qualitative Screening 5
36 | Dual Fuel (Add-On) Heat Pump Split System Energy Star | assume this involves adding heat pump to existing furnace, which will be used as back-up heat. Model an 11 SEER a/c system as base and retrofit will be 14.5 SEER, price retrofit kit as 16 SEER | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 0.16021 | 0.83802 | 0.19118 | 0.16491 | NO
37 | Air Source Heat Pump (16.0 SEER) Energy Star (CEE Tier 3) |  | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 0.75184 | 0.73438 | 1.0238 | 0.77664 | NO
38 | Air Source Heat Pump Split System Energy Star | 14.5 SEER (base case is std eff HP) | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 1.0967 | 0.76536 | 1.433 | 1.1317 | YES | 384.84 | 0.091561 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 307 | Rheem Prestige Series 3.0 ton 14.5 SEER Complete System R-410A with 80% Efficient 70k BTUH Gas Furnace (Multipoise) http://www.expressoverstock.com/rheem-prestige-series-3-0-ton-14-5-seer-complete-system-r-410a-with-80-efficient-70k-btuh-gas-furnace.html | 336.7002 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
39 | Air Source Heat Pump Package System Energy Star | 14.5 SEER (base case is std eff HP) | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes | Standard has increased from 12 SEER to 14.5 SEER | 0.69957 | 0.842 | 0.83084 | 0.72009 | NO
40 | Dual Fuel Heat Pump Package System Energy Star | 14.5 SEER (base case is std eff HP) | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 3.3062 | 0.83802 | 3.9453 | 3.4032 | YES | 250.14 | 0.087595 | GPC EnerSim model | 1 unit, HP home | MF | MF, MH | 77 | Air Source Packaged Heat Pump Prices plus cost of Deal Fuel Add on | 254.5779 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
41 | Dual Fuel Heat Pump Split System Energy Star | 14.5 SEER (base case is std eff HP) | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 0.425 | 0.83802 | 0.50715 | 0.43747 | NO
42 | AC Split Systems Energy Star | 14.5 SEER | Cooling - Central Air | [8 empty] | Yes |  | 0.82778 | 1.0899 | 0.75947 | 0.84736 | NO
43 | AC Package Systems, Energy Star | 14.5 SEER | Cooling - Central Air | [8 empty] | Yes |  | 0.11692 | 1.0899 | 0.10727 | 0.11968 | NO
44 | Ductless Air Conditioner | alternate measure for room air conditioner | Cooling - Room Air | [8 empty] | No | Better measure is VRF which has the additional capability of simultaneous heating and cooling. | bar: Qualitative Screening 3
45 | Geothermal Heat Pump, Closed Loop 3.3 COP/14.1 EER Energy Star |  | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 0.24686 | 0.7606 | 0.32456 | 0.25534 | NO
46 | Geothermal Heat Pump, DX 3.5 COP/15 EER Energy Star |  | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 0.21143 | 0.76921 | 0.27487 | 0.21861 | NO
47 | Geothermal Heat Pump, Open Loop 3.6 COP/16.2 EER Energy Star |  | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | Yes |  | 0.83501 | 0.76954 | 1.0851 | 0.86329 | NO
48 | Duct Testing & Sealing |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 1.2448 | 0.68623 | 1.8139 | 1.291 | YES | 737.51 | 0.0351 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 472 | 8 tube of calk $5 (http://www.google.com/products/catalog?q=duct+sealant&hl=en&client=firefox-a&hs=bAG&rls=org.mozilla:en-US:official&prmd=ivns&bav=on.2,or.r_gc.r_pw.&biw=1440&bih=719&um=1&ie=UTF-8&tbm=shop&cid=5476695973378092541&sa=X&ei=qXIpTtHPIYPegQee | 587.5282 | 18 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
49 | Duct insulation |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes |  | 0.22192 | 0.82624 | 0.26859 | 0.22887 | NO
50 | Locating Ducts inside conditioned spaces | Ducts in unconditioned spaces can lose 20-35% of energy. | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | No | This measure is only feasible for certain types of house designs | bar: Qualitative Screening 5
51 | Duct design/compact ducts |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes |  | 0.4652 | 0.68518 | 0.67895 | 0.48253 | NO
52 | Indirect/direct air cooling (IDAC - 2 stage Evap system) |  | Cooling - Central Air, Cooling - Heat Pump | [8 empty] | No | Not good applicability due to GA's high wet bulb temps (high humidity) | bar: Qualitative Screening 1; Qualitative Screening 5
53 | Active solar space heating |  | Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.02927 | 0.5897 | 0.049635 | 0.030466 | NO
54 | Active solar cooling |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | Does not appear to have widespread applicability or availability at the current time for residential use (often used for larger industrial applications) | bar: Qualitative Screening 4 to Qualitative Screening 5
55 | HVAC Lattice/Landscaping Shading |  | Cooling - Central Air, Cooling - Heat Pump | [8 empty] | No | Difficult to quantify savings - depends on orientation and amount of shading | bar: Qualitative Screening 1; Qualitative Screening 5
56 | Room/PTAC AC Energy Star | Energy Star level is 10% greater than federal std - varies from EER of 9.4 to 10.8 depending on unit size | Cooling - Room Air | [8 empty] | Yes |  | 3.0246 | 0.88982 | 3.3991 | 3.1037 | YES | 107.25 | 0.083629 | GPC EnerSim model | 1 unit, GH home | SF | SF, MF, MH | 33 | Change determined from 15000 BTU GE Zoneline PTAC Air Conditioner Electric Heat Unit AZ29E15DAC with Corrosion Protection http://www.ecoairandwater.com/store/15000-btu-ge-zoneline-ptac-air-conditioner-electric-heat-unit-az29e15dac-with-corrosion-protection.html | 99.8111 | 9 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
57 | Room air conditioner recycling |  | Cooling - Room Air | [8 empty] | Yes |  | 999.99 | 0.69533 | 999.99 | 999.99 | YES | 166.33 | 0.13051 | GPC EnerSim model | 1 unit, GH home | SF | SF, MF, MH | 0 | No equipment cost. | 61.1401 | 4 | USE 4 EUL BASED ON HALF OF REFRECYC; IC STILL 0; MODELED AS 'EARLY REPLACEMENT' | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
58 | Downsizing central air conditioner | this may be possible for existing homes with oversized units or homes that have implemented other measures that reduce the required load | Cooling - Central Air | [8 empty] | No | Appropriate sizing is a better measure. (#63) | bar: Qualitative Screening 1; Qualitative Screening 3
59 | Downsizing Heat Pump |  | Cooling - Heat Pump, Heat - Heat Pump | [8 empty] | No | Appropriate sizing is important to maximize efficiency, but it is difficult to estimate how oversized existing units are on average | bar: Qualitative Screening 1; Qualitative Screening 5
60 | HVAC Diagnostics and Servicing |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes |  | 9.4684 | 0.94649 | 9.6139 | 9.5329 | YES | 407.8 | 0.31361 | GPC EnerSim model | 1 unit, GH home | SF | SF, MF, MH | 169 | Cost of diagnostics plus 1 lb. Refrigerant | 1600.1638 | 10 | DEER EUL_Summary_10-1-08 copied refrigerant charge and duct sealing | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 134.32 | 0 | LO_Fast
61 | ECM Motor for HVAC equip (A/C, HP, & furnace) | ECM motors can save over 60% of electricity used by std motors | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes |  | 1.5576 | 0.84772 | 1.8374 | 1.6025 | YES | 156.78 | 0.059012 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 106 | This motor pricing based on Condensing unit. http://www.comfortgurus.com/product_info.php/products_id/7776 All else through RSMeans | 165.1015 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
62 | A/C filter replacement/cleaning |  | Cooling - Central Air, Cooling - Heat Pump | [8 empty] | Yes |  | 0.010436 | 0.056326 | 0.18528 | 0.014117 | NO
63 | Appropriately sized central air conditioner |  | Cooling - Central Air | [8 empty] | No | Code requirement | bar: Qualitative Screening 2
64 | Programmable Thermostat |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 1.6378 | 0 | 31.1235 | 1.6549 | YES | 99.07 | 0.84883 | GPC EnerSim model | 1 unit, GH home | SF | SF, MF, MH | 17 | Hunter Fan Company 44360 7-Day Energy Star Programmable Thermostat http://www.amazon.com/Hunter-Company-44360-Programmable-Thermostat/dp/B0002SP6AY/ref=sr_1_2?s=hi&ie=UTF8&qid=1317149017&sr=1-2 | 177.9387 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 43.79 | 0 | LO_Medium
65 | Clock thermostat | typically has a day/night setting | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | No | Programmable thermostat is better measure (#64) | bar: Qualitative Screening 3
66 | Whole House Fans |  | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | No | Savings depend on customer behavior. Poor customer acceptance due to indoor air quality issues caused by the fan. | bar: Qualitative Screening 1; Qualitative Screening 6
67 | Ceiling fan (Energy Star) |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 1.2092 | 1.1139 | 1.0855 | 1.239 | YES | 36.23 | -1.0675e-08 | GPC EnerSim model | 2 fans, HP home | SF | SF, MF, MH | 50 | Used GPC incremental cost | 60.4589 | 20 | DEER EUL_Summary_10-1-08, copied whole house fan | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
68 | Weatherization Measures kit | Provide customers kits containing weather stripping, door sweeps, caulk, foam sealant, and clear patch tape | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 6.6712 | 0.64425 | 10.355 | 6.9118 | YES | 984.2 | 0.13199 | GPC EnerSim model | 10 weather strips, 1 tube of caulk, HP home | SF | SF, MF, MH | 81 | Change based on 10 Weather Stripping Tape (http://www.homedepot.com/webapp/wcs/stores/servlet/ProductDisplay?R=100090883&N=5yc1vZard7&catalogId=10053&storeId=10051&langId=-1) and Polyseamseal 10 oz. Ultra Exterior Multipurpose Sealant (http://www.homedepot.com/h_d1/N-5yc1v/R-202192560/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053) | 540.3668 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
69 | Window and Wall A/C winterization kit | install winterization kits for low-income customers | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 2.1389 | 0.6319 | 3.3849 | 2.2177 | YES | 305.91 | 0.033405 | GPC EnerSim model | 10 weather strips, HP home | SF | SF, MF, MH | 76 | Change based on 10 Weather Stripping Tape (http://www.homedepot.com/webapp/wcs/stores/servlet/ProductDisplay?R=100090883&N=5yc1vZard7&catalogId=10053&storeId=10051&langId=-1). | 162.5577 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
70 | Compact Fluorescent - Exterior (Screw-in lamp) Energy Star |  | Lighting | [8 empty] | Yes |  | 4.7822 | 0.52793 | 9.0583 | 4.9539 | YES | 402.97 | 0 | GPC EnerSim model | 5 lamps | SF | SF, MF, MH | 41 | Change is equivalent CF (http://www.amazon.com/47448-29-Watt-150-Watt-equivalent-Energy/dp/B000WUEP9U/ref=sr_1_2?ie=UTF8&qid=1311341919&sr=8-2) | 196.0692 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
71 | Compact Fluorescent - Interior (Screw-in lamp) Energy Star |  | Lighting | [8 empty] | Yes |  | 12.7425 | 0.52185 | 24.4179 | 13.2192 | YES | 1032.62 | 0.13802 | GPC EnerSim model | 20 lamps | SF | SF, MF, MH | 23.28 | http://www.homedepot.com/Electrical-Light-Bulbs-CFL-Light-Bulbs/h_d1/N-5yc1vZbmat/R-100687001/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053 | 296.6452 | 5 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | CFL
72 | Torchiere Floor Lamps (Energy Star) | replace halogen torchiere lamp | Lighting | [8 empty] | Yes |  | 1.8714 | 0.4539 | 4.1229 | 1.9496 | YES | 122.31 | 0.012465 | GPC EnerSim model | 2 lamps | SF | SF, MF, MH | 4 | Change from http://www.amazon.com/Good-Earth-Lighting-GL6543-BK-GLI-Torchiere/dp/B000ZPMFC6/ref=sr_1_1?s=hi&ie=UTF8&qid=1313008018&sr=1-1 | 18.2191 | 5 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -2.73 | 0 | LO_Fast
73 | Compact Fluorescent - Interior (Hard-Wired Fixture) Energy Star |  | Lighting | [8 empty] | Yes |  | 2.0076 | 0.63526 | 3.1602 | 2.077 | YES | 1244.36 | 0.13795 | GPC EnerSim model | 20 fixtures | SF | SF, MF, MH | 153 | Change is equivalent CF (http://www.amazon.com/47448-29-Watt-150-Watt-equivalent-Energy/dp/B000WUEP9U/ref=sr_1_2?ie=UTF8&qid=1311341919&sr=8-2) | 674.9676 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -28.43 | 0 | LO_Fast
74 | Compact Fluorescent - Exterior (Hard-Wired Fixture) Energy Star |  | Lighting | [8 empty] | Yes |  | 5.0659 | 0.57876 | 8.7531 | 5.2438 | YES | 402.97 | 0 | GPC EnerSim model | 5 fixtures | SF | SF, MF, MH | 58 | TCP 33046 - 33014M Twist Pin Base Compact Fluorescent Light Bulb http://www.amazon.com/TCP-33046-33014M-Compact-Fluorescent/dp/B001Q8V3MY/ref=sr_1_2?s=hi&ie=UTF8&qid=1318523668&sr=1-2 | 293.8226 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
75 | Energy Star Decorative Light Strings | primarily LEDs - save 75% over incandescent lights | Lighting | [8 empty] | Yes |  | 0.92166 | 0.60583 | 1.5213 | 0.95543 | NO
76 | LED replacement for incandescent bulbs | LED lighting | Lighting | [8 empty] | Yes |  | 1.0209 | 0.65013 | 1.5703 | 1.0553 | YES | 1427.95 | 0.149 | GPC EnerSim model | 20 lamps | SF | SF, MF, MH | 753 | Change from http://www.homedepot.com/webapp/wcs/stores/servlet/ProductDisplay?storeId=10051&productId=202530170&langId=-1&catalogId=10053&ci_src=14110944&ci_sku=202530170&cm_mmc=shopping-_-googlebase-_-D27X-_-202530170&locStoreNum=159 | 777.0156 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -32.5 | 0 | LO_Slow
77 | Linear Fluorescent Electronic Ballasts |  | Lighting | [8 empty] | No | Better Measure is T8 or T5 linear fluorescent lamps with electronic ballasts (#78) | bar: Qualitative Screening 3
78 | T8 or T5 linear fluorescent lamps with electronic ballasts | replacing T12 fixtures and magnetic ballasts | Lighting | [8 empty] | Yes |  | 4.5907 | 0.98147 | 4.6774 | 4.707 | YES | 170.94 | -3.4468e-08 | GPC EnerSim model | 2 lamps | SF | SF, MF, MH | 0 | Change is T8 with electric ballast (http://www.amazon.com/72110-GE140RS120-DIY-ProLine-Electronic-Ballast/dp/B001OO9J58/ref=sr_1_1?ie=UTF8&qid=1311342672&sr=8-1) 1 lamp | 165.2935 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -3.77 | 0 | LO_Medium
79 | HID Fixtures - pulse start | includes metal halide and high-pressure sodium replacing incandescent or mercury vapor fixtures | Lighting | [8 empty] | Yes |  | 4.8952 | 0.5715 | 8.5655 | 5.0673 | YES | 402.97 | 0 | GPC EnerSim model | 2 lamps | SF | SF, MF, MH | 57 | Change (http://www.amazon.com/TCP-HOR-PS-250-Watt-Halide/dp/B001JEPKI8/ref=sr_1_1?s=hi&ie=UTF8&qid=1311342181&sr=1-1) | 279.026 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
80 | Ceramic Metal Halide | replacing incandescent, halogen, or halogen infrared fixtures | Lighting | [8 empty] | Yes |  | 0.26938 | 0.97261 | 0.27696 | 0.27625 | NO
81 | Occupancy sensor |  | Lighting | [8 empty] | Yes |  | 2.3064 | 0.73037 | 3.1579 | 2.375 | YES | 392.39 | -0.0003279 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 96 | Change is (http://www.amazon.com/Leviton-ODS10-ID-Decora-Switch-Occupancy/dp/B0007N72P6/ref=sr_1_2?ie=UTF8&qid=1301581139&sr=8-2) | 296.7135 | 15 | Based on life of Electronic Controls ASHRAE 2011 Life Estimate table. | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -4.72 | 0 | Medium
82 | Photocells | light sensors to shut off exterior lights in the daytime | Lighting | [8 empty] | Yes |  | 4.0945 | 0.57045 | 7.1775 | 4.2384 | YES | 473.04 | 0 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 80 | Change is (http://www.amazon.com/Thomas-Betts-Carlon-Photocell-HS525/dp/B00111C064/ref=sr_1_1?s=hi&ie=UTF8&qid=1312983926&sr=1-1) | 327.5572 | 15 | Based on life of Electronic Controls ASHRAE 2011 Life Estimate table. | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
83 | solar powered exterior lighting |  | Lighting | [8 empty] | Yes |  | 1.8051 | 0.5056 | 3.5703 | 1.8708 | YES | 525.6 | 0 | GPC EnerSim model | 5 fixtures | SF | SF, MF, MH | 115 | Change is LED solar lights from (http://www.amazon.com/Pine-Top-511-0007-Four-Light-Plastic/dp/B001V5IZEG/ref=sr_1_17?s=hi&ie=UTF8&qid=1301581453&sr=1-17) | 207.5914 | 8 | http://www.osti.gov/bridge/servlets/purl/755637-oDWEJR/webviewable/ or DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
84 | time clocks |  | Lighting | [8 empty] | No | Better Measure is Photocells (#82) | bar: Qualitative Screening 3
85 | Energy Star Ventilation Fan | Range hoods, bathroom/utility room vent fans, in-line vent fans | Other | [8 empty] | Yes |  | 2.4186 | 0.64174 | 3.7688 | 2.4971 | YES | 105.68 | 0.0037 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 25 | Hunter 82032 Energy Star 110 CFM Bathroom Fan for change. | 60.4652 | 10 | ASHRAE | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
86 | Dehumidifier - Energy Star | uses at least 10% less energy | Other | [8 empty] | Yes |  | 2.8821 | 0.56733 | 5.0802 | 2.984 | YES | 308.47 | 0.048197 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 59 | Change is DEP740EW - EdgeStar 74 Pint Portable Energy Star Dehumidifier - White http://www.compactappliance.com/DEP740EW-EdgeStar-74-Pint-Portable-Dehumidifier/DEP740EW,default,pd.html | 170.0453 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
87 | Room Air Cleaner - Energy Star | uses at least 35% less energy | Other | [8 empty] | Yes |  | 1.2856 | 0.54115 | 2.3758 | 1.333 | YES | 360.8 | 0.045077 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 70 | Change is Blueair 210B Energy-Star HEPASilent Air Purifier. http://www.amazon.com/Blueair-210B-Energy-Star-HEPASilent-Purifier/dp/B001KN6SDY/ref=sr_1_16?ie=UTF8&qid=1312901176&sr=8-16 | 107.5875 | 9 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -7.8 | 0 | LO_Medium
88 | Pool Pump Timer | set timer to run off-peak | Other | [8 empty] | Yes | Recommended measure by DOE - reducing pump run time will not degrade water quality | 7.2038 | 0.53825 | 13.3836 | 7.5102 | YES | 1104 | 0 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 86 | RSMeans Electric Timer | 619.5262 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
89 | Reduce Pool Filtration Pump runtime seasonally | reduce filtration run time (needs to run a minimum of ~4 hrs/day) | Other | [8 empty] | Yes |  | 999.99 | 0.55747 | 999.99 | 999.99 | YES | 2715 | 0 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 0 | No equipment cost. | 1154.6951 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
90 | high efficiency pool pump (single speed, two speed, variable speed) |  | Other | [8 empty] | Yes |  | 3.1266 | 0.8692 | 3.5971 | 3.2142 | YES | 1600.8 | 0.87 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 464 | Change http://www.amazon.com/Pentair-011013-IntelliFlo-High-Performance-Pool/dp/B002ALQAR4/ref=sr_1_8?ie=UTF8&qid=1301591951&sr=8-8 | 1450.7533 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
91 | Pool Cover | conserves heat and water, keeps pool cleaner which reduces filter run time | Other | [8 empty] | No | Limited applicability because only a portion of residential pools in GA are heated. Also difficult to quantify savings because pool heaters may only be used a portion of the year | bar: Qualitative Screening 1; Qualitative Screening 5
92 | Solar Pool Heater | Water can be diverted to a solar collector through the pool's filtration system before returning water to the pool | Other | [8 empty] | No | Limited applicability because only a portion of residential pools in GA are heated. Also difficult to quantify savings because pool heaters may only be used a portion of the year | bar: Qualitative Screening 1; Qualitative Screening 5
93 | Real-time handheld energy monitor | handheld monitor reads real-time electric consumption and provides actual cost per hour based on instantaneous consumption, which encourages homeowner to make voluntary choices to save (turn lights, appliance, equipment off) | Other | [8 empty] | No | Difficult to quantify actual savings and persistence of savings | bar: Qualitative Screening 1; Qualitative Screening 5
94 | Energy efficiency kits (CFLs, furnace whistles) | package of energy efficient devices to give away | Lighting, Electric Water Heater | [8 empty] | Yes |  | 9.1349 | 0.53066 | 17.2141 | 9.4734 | YES | 564.11 | 0.086877 | GPC EnerSim model | 12 lamps and 1 furnace whistle | SF | SF, MF, MH | 18 | 12 60Watt CFL replacements (http://www.amazon.com/GE-13-Watt-Energy-SmartTM-replacement/dp/B000NISDNU/ref=sr_1_1?s=hi&ie=UTF8&qid=1311344394&sr=1-1) and Furnace whistle (http://www.amazon.com/AM-Conservation-Group-Furnace-Whistle/dp/B004Z0SYO0/ref=sr_1_1?s=hi&ie=UTF8&qid=1311344458&sr=1-1) for Change. | 164.4277 | 5 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
95 | Low-flow toilets | conserve water, which would reduce pumping and WW treatment (saving energy at plant) | N/A (No residential energy savings) | [8 empty] | No
96 | PV System | pv system to reduce energy consumption from grid | **WHOLE HOME** | [8 empty] | No | outside the scope of energy efficiency analysis
97 | RIM Joists Insulation |  | Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 0.042168 | 1.0566 | 0.039909 | 0.043274 | NO
98 | Foundation/Slab Insulation |  | Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.15024 | 1.2217 | 0.12298 | 0.15367 | NO
99 | RIM Joists Insulation |  | Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | Duplicate of ID Number 97
100 | Ceiling Insulation R0 - R30 | for gas heat in GA, Energy Star website recommends R-22 to R-38 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 3.9254 | 0.88586 | 4.4312 | 4.041 | YES | 6582.08 | 2.0702 | GPC EnerSim model | 2,200 sq ft, HP home | SF | SF, MF, MH | 1962 | Change from RSMeans for given R insulation. | 7701.6439 | 20 | DEER EUL_Summary_10-1-08 copied floor insulation measure | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
101 | Ceiling Insulation R11 - R30 | for gas heat in GA, Energy Star website recommends R-22 to R-38 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". Also known as 'Attic Insulation'. | 1.3109 | 0.94546 | 1.3865 | 1.3476 | YES | 1436.55 | 0.52823 | GPC EnerSim model | 2,200 sq ft, HP home | SF | SF, MF, MH | 1390 | Change from RSMeans for given R insulation. | 1822.1383 | 20 | DEER EUL_Summary_10-1-08 copied floor insulation measure | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
102 | Ceiling Insulation R19 - R30 | for gas heat in GA, Energy Star website recommends R-22 to R-38 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". Also known as 'Attic Insulation'. | 0.66959 | 0.95187 | 0.70345 | 0.68828 | NO
103 | Ceiling Insulation R30 - R38 | for gas heat in GA, Energy Star website recommends R-22 to R-38 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". Also known as 'Attic Insulation'. | 0.29857 | 0.95041 | 0.31415 | 0.30691 | NO
104 | Ceiling Insulation R30 - R49 | for gas heat in GA, Energy Star website recommends R-22 to R-38 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". Also known as 'Attic Insulation'. | 0.32832 | 0.95356 | 0.3443 | 0.33748 | NO
105 | Storm Door | effective measure for wooden doors | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.75345 | 0.71473 | 1.0542 | 0.78065 | NO
106 | Thermal Door (Energy Star) | insulated wooden door - core filled with either fiberglass or rigid foam insulation | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.051574 | 0.64492 | 0.079969 | 0.053623 | NO
107 | ENERGY STAR glass door |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.1529 | 0.6259 | 0.24429 | 0.15911 | NO
108 | Floor Insulation R0 - R19 | for gas heat in GA, Energy Star website recommends R-11 to R-13 or R-13 to R-25 (depending on north or south) | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 2.8408 | 0.62688 | 4.5316 | 2.9559 | YES | 6127.46 | 0.22976 | GPC EnerSim model | 2,200 sq ft, HP home | SF | SF, MF, MH | 1550 | Change from RSMeans for given R insulation. | 4403.2492 | 20 | DEER EUL_Summary_10-1-08 copied floor insulation measure | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
109 | Infiltration Reduction Air Sealing |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 0.74057 | 0.63918 | 1.1586 | 0.76744 | NO
110 | Passive Solar Design | daylighting, trombe walls, sunspaces | Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | difficult to quantify savings - based on orientation and design | bar: Qualitative Screening 1; Qualitative Screening 5
111 | Radiant Barrier |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes | Studies have shown savings of 5-15% of cooling load | 0.59317 | 0.95258 | 0.62269 | 0.60968 | NO
112 | Energy Star Reflective Roof Products | cool roof | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes |  | 0.16028 | 0.6985 | 0.22947 | 0.16542 | NO
113 | Shade Trees |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | difficult to quantify savings - based on building orientation and amount of shading | bar: Qualitative Screening 1; Qualitative Screening 5
114 | Energy Recovery Ventilation (ERV) |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes |  | 0.79856 | 1.0534 | 0.79225 | 0.80176 | NO
115 | Attic Ventilator fan | electrically powered vent fan not recommended by Southface | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | electric attic vents may actually increase energy use - better measure is ridge vent (#117) | bar: Qualitative Screening 3
116 | Solar Attic Vent |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes |  | 0.65808 | 1.1821 | 0.55669 | 0.67421 | NO
117 | Ridge Vent |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes |  | 0.43413 | 0.89599 | 0.48452 | 0.44641 | NO
118 | Window Sun Screens | made from fabric and installed on the exterior window can absorb 65 to 70 percent of the solar heat | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | Yes |  | 0.18342 | 0.60631 | 0.30252 | 0.19028 | NO
119 | Energy Star Windows (U=.4 SHGC=.4) | from Energy Star website for South/Central US | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.16876 | 0.76204 | 0.22146 | 0.17446 | NO
120 | High Performance Windows (U=.32 SHGC=.30, low-e) |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.17206 | 0.83349 | 0.20643 | 0.17739 | NO
121 | Storm Windows (single pane base) |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.47539 | 0.70712 | 0.6723 | 0.49273 | NO
122 | Window Film |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.54099 | 0.65468 | 0.82633 | 0.55974 | NO
123 | ENERGY STAR skylight |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 4.4663 | 0.62822 | 7.1094 | 4.6476 | YES | 142.84 | 0.0042058 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 23 | Change: http://www.lowes.com/pd_317860-58-FS+C06+2005_4294937086__?productId=3280996&Ntt=skylight&pl=1&currentURL=%2Fpl_Windows%2BDoors_4294937086__s%3FNtt%3Dskylight | 102.7238 | 20 | DEER EUL_Summary_10-1-08, copied ES window | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
124 | Thermal Drapes |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | difficult to quantify savings for this measure - depends on type of drapes and customer usage patterns. | bar: Qualitative Screening 1
125 | Wall Insulation R0 - R11 | for gas heat in GA, Energy Star website recommends R-11 to R-22 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.66367 | 0.12972 | 5.116 | 0.69167 | NO
126 | Wall Insulation R13 - R19 | for heat pump in GA, Energy Star website recommends R-11 to R-22 | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.11998 | 0.59872 | 0.20039 | 0.12504 | NO
127 | Attic kneewall - insulation and airsealing |  | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 2.6336 | 1.4002 | 2.2828 | 2.6587 | YES | 159.92 | 0.16041 | GPC EnerSim model | 450 sq ft, GH home | SF | SF, MF | 305 | Change is below material cost along with drywall and painting from RSMeans. OWENS CORNING E20 FLOORS AND WALLS INSULATION R19 KF 23X94 http://www.amazon.com/18324-Seal-Removable-Caulk-10-1-Ounce/dp/B0002YVNOQ/ref=cm_cr_pr_product_top,%20http://www.amazon.com/OWENS-CORNING-E20-FLOORS-INSULATION/dp/B001G7KXXU | 803.2436 | 20 | DEER EUL_Summary_10-1-08, copied wall insulation | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 28.5 | 0 | LO_Medium
128 | Water Heater Audit (Includes Insul. Jacket, Aerator, Low-flow Showerhead, Pipe Insulation |  | Electric Water Heater | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 6.9402 | 0.61129 | 9.3118 | 7.0732 | YES | 390.92 | -0.0078157 | GPC EnerSim model | WH jacket, aerator, showerhead, 3 ft pipe insulation | SF | SF, MF, MH | 68 | http://www.amazon.com/B5-69-WATER-HEATER-INSULATION-JACKET/dp/B002FYKSCE, http://www.amazon.com/ACE-MALE-FAUCET-AERATOR-thread/dp/B000H5ZZOY, http://www.amazon.com/American-Standard-1660-717-002-Water-Saving-Showerhead/dp/B00125V740/ref=sr_1_5?s=hi&ie=UTF8&qid=1301698699&sr=1-5, http://www.amazon.com/Duck-1285241-0-75-Inch-3-Feet-Insulating/dp/B002GKC2VM/ref=pd_sxp_f_r | 471.9324 | 13 | DEER EUL_Summary_10-1-08, copied pipe insulation | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 3165.3615 | Fast
129 | Water Heater Timer | turns water heater off at night and on in the morning | Electric Water Heater | [8 empty] | Yes |  | 1.8569 | 2.0597 | 0.90155 | 1.9372 | YES | 70.9 | 0 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 74 | Change from RSMeans Switch devices, resi, interval timer wall switch, 1-30 min., #12/2, type NM cable, 20', 20 amp, incl box & cover plate. | 137.4142 | 11 | DEER EUL_Summary_10-1-08, copied time clock | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
130 | Water heater Direct Load Control |  | Electric Water Heater | [8 empty] | Yes |  | 0 | 0 | 999.99 | 0 | NO
131 | Water Heater Heat Trap |  | Electric Water Heater | [8 empty] | No | Similar savings achieved with Pipe Insulation (#139) and avoiding plumber installation | bar: Qualitative Screening 3
132 | Integral Heat Pump Water Heater |  | Electric Water Heater | [8 empty] | Yes* | recommended measure by DOE in moderate climates; Program currently in place-"Georgia Power Home Energy Improvement Program". | 1.405 | 0.61454 | 2.2862 | 1.4537 | YES | 1909.61 | 0.050326 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 727 | Change from http://www.homedepot.com/h_d1/N-5yc1v/R-202552735/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053 | 1021.4087 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
133 | High Efficiency Water Heater - 50 gal. EF= .94 (base=.86) | Energy Star does not rate water heaters | Electric Water Heater | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 0.62456 | 0.64022 | 0.97553 | 0.64613 | NO
134 | Instantaneous Hot Water System | also known as tankless | Electric Water Heater | [8 empty] | Yes |  | 2.1986 | 0.66371 | 3.3127 | 2.2769 | YES | 805.31 | 0.042549 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 333 | Used 2010 prices | 732.1446 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
135 | Solar Water Heater |  | Electric Water Heater | [8 empty] | Yes* | Program currently in place-"Georgia Power Home Energy Improvement Program". | 1.3848 | 0.75395 | 1.5967 | 1.4056 | YES | 1605.89 | 0.092779 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 2170 | Change from RSMeans Page 501 System D2020 280 2820 Part Q: Collector panel Solar energy system + Tank | 3004.9799 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 21197.0715 | LO_Slow
136 | Storage Water Heater (Off peak heating) |  | Electric Water Heater | [8 empty] | Yes |  | 0 | 0 | 0.23276 | 0 | NO
137 | Drain Heat Exchanger |  | Electric Water Heater | [8 empty] | Yes | recommended measure by DOE | 0.68908 | 0.72225 | 0.95406 | 0.71306 | NO
138 | Heat Recovery Water Heater With Heat Pump |  | Electric Water Heater | [8 empty] | Yes |  | 1.4434 | 0.63628 | 2.2685 | 1.4942 | YES | 2703.73 | 0.28118 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 1336 | Change from RSMeans lookup for copper piping, and online lookup for desuperheater. | 1928.3705 | 14 | DEER EUL_Summary_10-1-08 Compressor Heat Recovery (w/electric water heating) | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Slow
139 | pipe insulation |  | Electric Water Heater | [8 empty] | Yes |  | 1.3252 | 0.62273 | 2.128 | 1.372 | YES | 40.55 | 0.014122 | GPC EnerSim model | 1 linear foot | SF | SF, MF, MH | 20 | Change is from RSMeans average of 3 pipe insulation types. | 26.5034 | 13 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Fast
140 | GSHP desuperheater | uses heat pump waste heat for water heating | Electric Water Heater | [8 empty] | Yes |  | 1.1818 | 0.65375 | 1.8077 | 1.2227 | YES | 2685.39 | 0.082661 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 1638 | Change from RSMeans lookup for copper piping, and online lookup for desuperheater. | 1935.7289 | 14 | DEER EUL_Summary_10-1-08 Compressor Heat Recovery (w/electric water heating) | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Slow
141 | In-Home Energy Use Displays | This measure relies on behavioral change brought about by showing the homeowner feedback information about energy consumption | Other | [8 empty] | No | Difficult to quantify actual savings and persistence of savings | bar: Qualitative Screening 1; Qualitative Screening 4
142 | Smart Premium (Robust) Residential Air Conditioners | Emerging Technology: This measure uses auto-diagnostic control technology to ensure that air conditioners will perform as efficiently as possible through the life of the product. | Cooling - Central Air | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
143 | Construction - ICF | Concrete Framing - New Construction | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | Limited to new construction only | bar: Qualitative Screening 1; Qualitative Screening 5
144 | Construction - SIP | Specialty Framing - New Construction | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | Limited to new construction only | bar: Qualitative Screening 1; Qualitative Screening 5
145 | Spray-in foam insulation | Major Remodel or New Construction, Will lower infiltration and increase the R-value. | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | Yes |  | 0.27812 | 0.95199 | 0.29215 | 0.28588 | NO
146 | MultiZone Thermostat | Allows for different setpoints in the home. | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | Requires multizone HVAC system or major duct/damper retrofit with complex control system | bar: Qualitative Screening 1; Qualitative Screening 5 to Qualitative Screening 6
147 | Green roof - vegetated rooftop | A green roof is a roof of a building that is partially or completely covered with vegetation and a growing medium, planted over a waterproofing membrane. Reduces building summer cooling loads by improving the insulation properties. | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air, Heating - Elec Furn, Heating - Room, Heat - Heat Pump | [8 empty] | No | Limited applicability | bar: Qualitative Screening 1; Qualitative Screening 5 to Qualitative Screening 6
148 | Behavioral changes from utility-provided information | Information is sent to homeowners comparing their consumption with homes in their neighborhood, which can influence their behavior | Other | [8 empty] | Yes |  | 999.99 | 0.5777 | 999.99 | 999.99 | YES | 508.07 | -0.038441 | GPC EnerSim model | 1 unit, HP home | SF | SF | 0 |  | 35.9636 | 1 | http://opower.com/uploads/library/file/10/brattle_mv_principles.pdf | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
149 | LED task lights | replacement of incandescent under cabinet lights | Lighting | [8 empty] | Yes |  | 2.2486 | 0.98935 | 2.2729 | 2.3058 | YES | 159.29 | -4.5644e-08 | GPC EnerSim model | 1 unit | SF | SF, MF, MH | 44 | Change is two from (http://www.amazon.com/LED-Under-Counter-Light-2040WH/dp/B002LMNWMI/ref=pd_bxgy_hi_text_c), one from (http://www.amazon.com/LED-Light-Flexible-Connector-2040CONN/dp/B002LMGM7A/ref=pd_bxgy_hi_text_b), and one from (http://www.amazon.com/LED-Power-Supply-Under-Counter/dp/B002LMQ6G2/ref=pd_sim_hi_1) | 153.524 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | -3.58 | 0 | LO_Medium
150 | Timer for recirculation pump | reduce usage of recirculation pump | Electric Water Heater | [8 empty] | Yes |  | 0.22548 | 0.36808 | 0.61258 | 0.23557 | NO
151 | Variable Refrigerant Flow Heat Pump | used to cool and homes where there is no existing ductwork. Ductless heat pumps can heat and cool your home. Dual-zone or triple-zone systems have two or three indoor units attached to one outdoor unit to cool large homes, Four zone VRV heat pump 3 ton, 15 SEER | Cooling, Heating | [8 empty] | Yes |  | 1.4244 | 0.51915 | 2.7438 | 1.4804 | YES | 3383.6888 | 0.41459 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 1255 | Change is from http://www.e-comfortusa.com/index.php?cPath=331_146_148_276_362&capacity_min=30000&capacity_max=40000&sort=3a&page=2 | 1787.6807 | 13 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Slow
152 | Consumer Energy Storage | Consumer deployed energy storage technology, currently used in combination with on-site renewable resources to mitigate inherent intermittency and to increase the value of photovoltaic(PV) and wind generated electricity. | Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
153 | Smart Appliances | Smart appliances can autonomously respond favorably to pricing signals and/or electric grid disturbances, such as loss of generation or sustained low voltage. Autonomously changes its operations cycle based on pricing changes to save money. | Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
154 | Home Area Networks | A home-area network(HAN) connects in-home digital devices, such as personal computers, mobile devices, telephones, televisions, video games, DVD players, thermostats, home security systems, smart appliances, or other digital devices in to a common network. Consumer enabling technology that allows them to specify how they will use energy by managing devices and appliances like smart thermostat, air conditioners, pool pumps. | Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
155 | Electric Vehicles/PHEVs | A plug-in hybrid electric vehicle (PHEV) is a hybrid vehicle with batteries that can be recharged by connecting a plug to an electric power source. It shares characteristics of conventional hybrid electric vehicles and battery electric vehicles, having an internal combustion engine in addition to batteries for power. | Other | [8 empty] | No | No electrical energy savings as baseline is gasoline powered vehicle. | bar: Qualitative Screening 1; Qualitative Screening 5
156 | Combined heat and power | Combined heat and power (CHP) is a specific form of distributed generation (DG) that refers to the strategic placement of electric-power-generating units at or near customer facilities to supply on-site energy needs. CHP enhances the advantages of DG by the simultaneous production of useful thermal and power output, thereby increasing overall efficiency. | Heating, Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
157 | Customer Gateways | Customer gateways allow consumers to become part of the smart grid by enabling self-service energy provisioning on the premises, linking and integrating consumer energy management, and having smart appliances increase energy efficiency and enhance the consumer's quality of life. | Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
158 | Efficient AC/DC conversion | SMPS type: A switched-mode power supply (switching-mode power supply, SMPS, or simply switcher) is an electronic power supply that incorporates a switching regulator in order to be highly efficient in the conversion of electrical power. | Other | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
159 | Low Temperature Heat Pump | High-performance heat pump at low temperatures; eliminating the need for backup heat. | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
160 | Residential hot-dry air conditioners | Equipment to optimize A/C, redesign to refrigeration and fan equipment | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | No commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
161 | Advanced (commercial A/C) modulating HVAC compressors | Modulating systems are rare, as most systems only have one speed, but competition and an expanded marketplace are changing that. Compressors use 55-80% of total energy for a roof-top unit | Cooling - Central Air, Cooling - Heat Pump, Cooling - Room Air | [8 empty] | No | limited commercial products available | bar: Qualitative Screening 1; Qualitative Screening 4
162 | Central A/C / Heat Pump Quality Installation Verification (QIV) | Quality Installation and Verification (QIV) is a standard developed by the Air Conditioning Contractors of America (ACCA) to ensure quality installation of central air conditioners, heat pumps and furnaces. | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes |  | 1.2269 | 0.63859 | 1.9212 | 1.2707 | YES | 334.73 | 0.048545 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 145 | No equipment cost. | 177.8946 | 10 | DEER EUL_Summary_10-1-08 copied refrigerant charge and duct sealing | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
163 | Energy Star imaging equipment |  | Other | [8 empty] | Yes | Combination of ID #'s 17, 19-21 | 0.072707 | 0.43192 | 0.16834 | 0.075607 | NO
164 | Boiler outdoor reset control | Reset of hot water setpoint in single and multi-family residential buildings with zone thermostat control. The measure is assumed to be applied to existing non-condensing boiler systems. | [9 empty] | No | Small saturation of residential boilers and fewer number or electric residential boilers. Better measure would be heat pump measures or gas heat. | bar: Qualitative Screening 3; Qualitative Screening 5
165 | TXV Valve Replacement from Fixed Orifice | A thermal expansion valve is a component in refrigeration and air conditioning systems that controls the amount of refrigerant flow into the evaporator thereby controlling the superheat at the outlet of the evaporator. Thermal expansion valves are often referred to generically as "metering devices". | Cooling- Central Air, Cooling - Heat Pump, Heating - Heat Pump | [8 empty] | No | Virtually all residential units produced in the last 10 years were shipped from the factory with TXV valves as standard equipment. Low number of applicable equipment which qualify for retrofit. | bar: Qualitative Screening 2; Qualitative Screening 5
166 | Room Air Conditioners Energy Star - Reverse Cycle/Heat Pump | Same as Room Air conditioner with the additional feature of reverse cycle for heating. | Cooling - Room Air, Heating - Room | [8 empty] | Yes |  | 2.3447 | 0.64992 | 3.6076 | 2.4283 | YES | 268.24 | 0.035099 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 69 | Friedrich X-Star Series XQ08M10 http://www.ajmadison.com/cgi-bin/ajmadison/XQ08M10.html | 161.7812 | 12 | Based on Residential single or split package AC Unit from ASHRAE 2011 Life Estimate table. | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
167 | AC Split Systems 16 SEER | Meets CEE Tier II | Cooling - Heat Pump, Heating - Heat Pump | [8 empty] | Yes |  | 0.29739 | 1.0947 | 0.27165 | 0.30442 | NO
168 | ECM circulating pumps | ECM motor on recirulating DHW pump | [9 empty] | Yes |  | 999.99 | 0.62604 | 999.99 | 999.99 | YES | 78.84 | 0.009 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF | 0 | This motor pricing based on Condensing unit. http://www.comfortgurus.com/product_info.php/products_id/7776 | 65.2558 | 18 | Based on Electric Motor from ASHRAE 2011 Life Estimate table. | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
169 | AC Split Systems 18 SEER | Third tier high efficiency central A/C system | [9 empty] | Yes | Added to have additional tier | 0.28094 | 1.0964 | 0.25625 | 0.28758 | NO
170 | Air Source Heat Pump (18.0 SEER) | Third tier high efficiency central heat pump system | [9 empty] | Yes | Added to have additional tier | 0.55473 | 0.74315 | 0.74647 | 0.57287 | NO
171 | HVAC Diagnostics and Servicing Heat Pump | Same as ID# 60 but for Heat Pump systems | Cooling - Central Air, Cooling - Heat Pump, Heating - Elec Furn, Heat - Heat Pump | [8 empty] | Yes | Added for Heat Pump seperately | 3.5579 | 0.74147 | 4.7985 | 3.669 | YES | 879.51 | 0.30652 | GPC EnerSim model | 1 unit, HP home | SF | SF, MF, MH | 169 | Cost of diagnostics plus 1 lb. Refrigerant | 601.288 | 10 | DEER EUL_Summary_10-1-08 copied refrigerant charge and duct sealing | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Fast
172 | Home Energy Management System | [10 empty] | Yes | Found similar device in market. No specific energy savings data available; will assume flat five percent savings for total metered load. | 0.20497 | 0.61177 | 0.33504 | 0.21212 | NO
173 | Highly Efficient Incandescent Light Bulbs | New Halogena incandescent bulb | [9 empty] | Yes |  | 0.58205 | 0.40513 | 1.4367 | 0.60922 | NO
174 | Gas Filled Panels | Gas Filled Panels (GFPs) are a new, advanced approach to ambient-temperature thermal insulation applications. They consist of infrared reflecting (low emissivity), multilayer baffles enveloped by a sealed barrier and filled with a low conductivity gas or air (at atmospheric pressure). | [9 empty] | No | No cost for product found. Commercial applications appear to still be in development and primary application appears to be in appliances, where savings would be accounted for in appliance efficiency level. http://gfp.lbl.gov/licensing.html | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
175 | Power Quality-Improving Appliances | Power Quality-Improving (PQI) Appliances are devices developed to manage appliance load profiles to improve overall power quality in terms of power factor and harmonics. | [9 empty] | No | This device adds small load to customer's home. No specific cost nor specific energy savings data available. Power quality improvement and power factor correction provides improvements to the reactive power required by inductive loads (electrical motors, fluorescent lighting, etc), which in turn reduces the apparent power required from the grid. However, these devices do not increase the efficiency or decrease the amount of working power (measured in watts) dissipated by an inductive load. Small kWh savings may be achieved through reduction in transmission line losses, but it is unclear how these savings relate to the additional small load added to the home. | bar: Qualitative Screening 1
176 | Thin-Film Lithium-Based Electrochromic Devices | Electrochromic cells change their light transmission characteristics based on the direction of an applied electric field. In short, they are comprised of an electrolyte sandwiched between two electrodes (a cathode and an anode), where each electrode will darken or bleach based on the flow of ions (and electrons) in or out of the electrode. For lithium-based electrochromic cells, the electrolyte contains mobile lithium which enables lithium ion transfer between the electrodes. The present technology provides both a cell structure and method for fabricating that structure yielding improved performance, cost and stability. | [9 empty] | No | No specific cost nor specific energy savings data available. This measure describes a technology that has potential for application to commercial products, such as windows, but does not appear to be fully developed into a specific product. | bar: Qualitative Screening 1; Qualitative Screening 4
177 | Light Emitting Diodes Based on Lattice-Mismatched GaInP AlloysI A new approach to fabricating green LEDs | Light emitting diodes are the promise of the future because, unlike tungsten bulbs or compact florescent bulbs, they deliver most of their energy as light, rather than heat. The U.S. Department of Energy expects to phase out tungsten bulbs by 2014, and compact fluorescents by 2020, leaving LEDs with virtually the entire market. Current white light generation techniques rely on color mixing from red, blue and green light. While reasonable red and blue LEDs are available for this scheme, availability of a good green LED poses a significant technological challenge. There currently exists a gap in the wavelength spectral window from roughly 530 nm to 570 nm, known as the “green gap,” where realization of efficient green LEDs is proving to be very difficult. | [9 empty] | No | No specific cost nor specific energy savings data available. This technology applies to manufacturing techniques for LED bulbs, but does not include a commercially available measure, nor describe a measure that produces additional energy savings beyond the other LED lighting measures already included in the catalog. | bar: Qualitative Screening 1; Qualitative Screening 4
178 | Compact Absorption Chiller | The Compact Absorption Chiller uses microchannel technologies in an absorption heat pump which produces cooling using heat as the primary energy source. | [9 empty] | No | No specific cost nor specific energy savings data available. Appears to be in the prototype/development phase but unclear if this will become a commercially available product for the residential market. | bar: Qualitative Screening 1; Qualitative Screening 4
179 | Low-cost, Modular, Building-integrated Photovoltaic-Thermal Collector | Buildings consume approximately 40% of the energy, and nearly 70% of the electricity used in the United States. Building surfaces are well suited to renewable energy production. The surface area of a typical residence is large enough to produce the electricity required to operate the building. However, in order to achieve net-zero energy use, solar thermal collectors are often required to produce hot water for domestic and space heating needs or pre-heated ventilation air. Current problems with the approach to building based renewable energy production: •Collectors are not integrated into the building surfaces and are not aesthetically pleasing. •Both systems remain separate, each with different mounting systems, resulting in added expense. •Because both systems are installed separately, total roof area required to meet electrical and hot water loads can exceed the roof area available. •When mounted flush to the roof, photovoltaics tend to overheat, reducing efficiency and annual output. •Collectors are durable enough to act as the building surface, but are typically installed over an existing building surface, resulting in unnecessary material use and added expense. | [9 empty] | No | This is a proposal for a graduate student's university research project. Solar PV applications that are currently commercially available are included as a separate measure in the catalog. | bar: Qualitative Screening 1; Qualitative Screening 4
180 | Alternating Current Photovoltaic Building Block ACE Plug-N-Play | This technology provides a fully integrated and self-containing alternating current (AC) photovoltaic (PV) Building Block device and method that allows photovoltaic applications to become true plug and play devices. The Building Block combines, contains, and integrates almost all of the electrical and mechanical elements of a PV system while eliminating the traditional DC voltage concerns of todays PV systems. | [9 empty] | No | No specific cost nor specific energy savings data available. Appears to be in prototype stage and this technology does not appear to provide additional or unique energy savings beyond the solar PV measures already being considered in the catalog. | bar: Qualitative Screening 1; Qualitative Screening 4
181 | Solid-State Phase Change Floor Tile for Use in Passive Solar Applications | Floor tiles incorporating a microencapsulation system underneath that contains a phase change material. The floor tile absorbs excess heat during the day, melting the phase change material. As temperatures cool in the evening, the phase change material solidifies, releasing the heat and warming the room. | [9 empty] | No | No specific cost nor specific energy savings data available. Appears to still be in prototype phase without cost estimates for commercial applications. Savings would largely depend on amount of floor area that utilizes tiles and their orientation for heat gain during the day. | bar: Qualitative Screening 1; Qualitative Screening 4
182 | Super Energy Saver Heat Pump | ORNL researchers developed a broad class of dynamic hybrid phase change materials and coupled them to residential heat pumps, inventing a super energy saver heat pump. This invention significantly improves heating/cooling efficiency in existing pumps and decreases greenhouse gases, due to reduced energy consumption. | [9 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1
183 | Water-Heating Dehumidifier | A small appliance developed at ORNL dehumidifies air and then recycles heat to warm water in a water heater. The device circulates cool, dry air in summer and warm air in winter. In addition, the invention can cut the energy required to run a conventional water heater by an estimated 50 per cent. | [9 empty] | No | Appears to still be in development stage. No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
184 | Energy Saving Absorption Heat Pump Water Heater | ORNL’s new absorption heat pump and water heater technology offers substantial energy savings and can reduce the use of fossil fuels by buildings. While conventional heat pump water heater designs are limited to using toxic ammonia water systems, this system uses heat drawn from the ambient environment to achieve energy efficiency. This approach extends the application of the invention beyond industrial settings to residential and commercial use. | [9 empty] | No | Appears to still be in development stage. No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
185 | Non-Invasive Energy Meter | Sandia has developed an energy monitoring device that measures energy from liquid flow systems (e.g., solar systems) using a simple technique that senses when the system is running and then estimates the BTU energy production. Current energy meters must be installed into the system to measure how much energy the system is producing or losing. This involves cutting pipes, installing thermal wells, and flow meters, and/or connecting sensors to pump motors in the system. This often requires licensed contractors and many solar systems are too small and the value of the energy they collect is not sufficient to justify a commercially available BTU meter. | [9 empty] | No | No specific cost nor specific energy savings data available. Appears to still be in prototype phase; also does not appear to only measure energy production and not produce any additional energy savings for a solar energy system. | bar: Qualitative Screening 1; Qualitative Screening 4
186 | Efficient Polymer Solar Cells | Ames Laboratory researchers have developed a process for producing more efficient polymer solar cells by increasing light absorption through a thin and uniform light-absorbing layer deposited on a textured substrate. | [9 empty] | No | No specific cost nor specific energy savings data available. Current polymer solar cells are approximately one third efficient than the current efficiency of hard materials (http://en.wikipedia.org/wiki/Polymer_solar_cell) | bar: Qualitative Screening 1; Qualitative Screening 4
187 | Highly Insulating Windows (R5+) | Windows which have U-values of <0.2 | [9 empty] | Yes | Highly Insulating Windows (R5+) | 0.098384 | 0.63461 | 0.15503 | 0.10235 | NO
188 | PCMs (Phase Change Materials) - Insulation | Encapsulated phase change materials (PCMs) consist of an encapsulated substance with a high heat of fusion. The phase change material absorbs and releases thermal energy in order to maintain a regulated temperature within a product such as textiles, building materials, packaging, and electronics. http://www.microteklabs.com/phasechange.html | [9 empty] | No | Could not find any sources for product. http://www.toolbase.org/Technology-Inventory/HVAC/phase-change-materials | bar: Qualitative Screening 1; Qualitative Screening 4
189 | High Performance Windows, Dynamic Windows, Advanced Window Films - Electrochromic Windows | The window changes from clear to tinted when a small electric field is applied and the lithium ions move into the working electrode layers. The change can be triggered by sensors in an automated building management system, or by a flick of a switch. Electrochromic windows can block as much as 98 percent of the direct sunlight. Reversing the polarity of the applied voltage causes the ions to migrate back to their original layer, and the glass returns to clear. http://www.nrel.gov/features/20100122_electrochromic.html | [9 empty] | No | Not currently available. Current Smart Windows are Liquid Crystal windows and require energy to maintain the transparent state. http://www.consumerenergycenter.org/home/windows/windows_future.html | bar: Qualitative Screening 1; Qualitative Screening 4
190 | High Performance Windows, Dynamic Windows, Advanced Window Films - Thermochromic Windows | As the prefix thermo- implies, heat causes thermochromic windows to alter their properties. In response to changes in the ambient temperature, clear thermochromic glazings becomes diffused. Several thermochromic technologies are being explored, but gel-based coatings seem to be the most promising. "Cloud Gel, " a product now on the market, is a thin plastic film that can be incorporated into almost any window assembly. The response temperatures of "Cloud Gel" can be adjusted depending on need and location. In addition to automatically changing from clear to diffused in response to heat, the glazings also turn white and reflective, reducing the transmission of solar heat. That can reduce air conditioning costs significantly when it's hot outside. Because you can no longer see through the window once it loses its transparency, this glazing is probably best suited for skylights rather than view windows. http://www.consumerenergycenter.org/home/windows/windows_future.html | [9 empty] | No | Could not find any source for Smart Windows which are specifically Thermochromic. Also this glass type turns completely white and oqaque when activated by its surroundings; therefore, as mentioned in description, applicability is likely limited to skylights rather than all windows. | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
191 | High Performance Windows, Dynamic Windows, Advanced Window Films - Gasochromic windows | Gasochromic windows produce a similar effect to electrochromic windows, but in order to color the window, diluted hydrogen (below the combustion limit of 3 percent) is introduced into the cavity in an insulated glass unit. Exposure to oxygen returns the window to its original transparent state. To maintain a particular state, the gap is simply isolated from further changes in gas content. The optically active component is a porous, columnar film of tungsten oxide, less than 1 micron thick. This eliminates the need for transparent electrodes or an ion-conducting layer. Variations in film thickness and hydrogen concentration can affect the depth and rate of coloration. http://www.commercialwindows.umn.edu/materials_tech3.php | [9 empty] | No | Could not find any source for Smart Windows which are specifically Gasochromic. http://www.commercialwindows.umn.edu/materials_tech3.php | bar: Qualitative Screening 1; Qualitative Screening 4
192 | TV Occupancy Sensor Power Strip | Reduce standby power of residential TVs | [9 empty] | Yes |  | 0.9124 | 0.53935 | 1.6917 | 0.94949 | NO
193 | Compact Fluorescent - Interior (Screw-in lamp) Energy Star with EISA Baseline | CFL replacing incandexcent bulb compliant with EISA standards that being phasing in in 2012 | Lighting | [8 empty] | Yes |  | 999.99 | 0.37916 | 999.99 | 999.99 | YES | 606.812 | 0.081105 | GPC EnerSim model | 20 lamps | SF | SF, MF, MH | 0 | http://www.homedepot.com/Electrical-Light-Bulbs-CFL-Light-Bulbs/h_d1/N-5yc1vZbmat/R-100687001/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053 | 174.3215 | 5 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | GPC Saturation Survey (2007), RECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
(1) Energy and demand savings for modeled/selected facility type
(2) Percentage of residential customers for modeled/selected facility type that measure or technology is applicable to, based on market share for the technology and applicability factors (technical feasibility, share for competing measures, measure contribution to end-use kWh consumption)
(3) Forecast of cumulative achievable potential (kWh savings) for an aggressive incentive scenario over period of potential study for all permutations (e.g. new & existing, all heating equipment types) of modeled/selected facility type

## Non-Residential
[13 empty] | PUBLIC DISCLOSURE | [13 empty] | PUBLIC DISCLOSURE | [9 empty] | PUBLIC DISCLOSURE
Georgia Power Company - 2013 IRP DSM - Technology Catalog - NonResidential | [13 empty] | Georgia Power Company - 2013 IRP DSM - Technology Catalog - NonResidential | [13 empty] | Georgia Power Company - 2013 IRP DSM - Technology Catalog - NonResidential
Measure Details |  | Description | Measure Categorization | Qualitative Screening | [9 empty] | Economic Tests |  |  |  |  | Energy/Demand Impacts | [5 empty] | Cost Impacts |  |  | Additional Measure Data
ID Number | DSM Measure Name | General Description | End-Use Category | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Pass to Economic Screen | Notes | TRC | RIM | PCT | SCT | Pass TRC? | Energy (kWh) savings (1) | Peak Coinc. Demand (kW) savings (1) | Savings Reference | Savings/ Modeling Notes | Modeled Facility Type | Applicable Facilities | Incremental Measure Cost | Cost Reference | Utility Avoided Cost (Lifetime) | Measure Life | Meas. Life Reference | Levelized cost per lifetime kWh | Size of eligible market (2) | Achievable Mkt Pen-Agg(3) | Current Saturation | Saturation Reference | Non-electric part. Benefits - gas (therms) | Non-electric part. Benefits - water (gal) | TEAPOT Ramp Rate
|  |  |  | Difficult to Quantify Savings | Current Practice | Better Measure Available | Immature or Unproven Technology | Limited Applicability | Poor Customer Acceptance | Health & Environ. Concerns | End-Use Service Degradation | [25 empty] | TEAPOT Ramp Rate
1 | Energy Star commercial dishwasher | 25% more energy efficient and 25% more water efficient than std models | Cooking | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 11.1768 | 0.53531 | 18.5344 | 11.4679 | Yes | 6687.18 | 0.49894 | GPC EnerSim model | 16kW base, 12 kW chg | Restaurant | Education, Hospital, Lodging, Restaurant, | 528 | Jet Tech F-18DP - Commercial Undercounter Dishwasher - High Temperature with Built-In Booster Heater - 24 Racks Pr Hr http://www.zesco.com/Jet-Tech-F-18DP-commercial-dishwasher-pz308D020.htm | 5915.2825 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -0.15 | 26878.5 | LO_Medium
2 | High-Efficiency Combination Oven | Cooks in three modes: steam, convection, and combination of both. Can save 39% over conventional oven | Cooking | [8 empty] | Yes |  | 0.7994 | 0.81673 | 0.97878 | 0.82615 | No
3 | LED Overhead Lighting (replacing metal halide canopy lights) | replace 400w metal halide with 60w LED | Indoor Lighting - C | [8 empty] | Yes |  | 2.1033 | 0.92891 | 2.2643 | 2.1821 | Yes | 102708.45 | 0 | GPC EnerSim model | 98 fixtures in facility | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 47225 | 60 Watt LED Street Lamp Wall Pack Canopy Soft Warm 3000K Type Bulb Retrofit Light HID http://www.shineretrofits.com/60-watt-led-street-lamp-wall-pack-canopy-soft-warm-3000k-type-bulb-retrofit-light-hid-hps-replacement-g120-s60dsc.html | 99328.9841 | 29 | DEER EUL_Summary_10-1-08 trending to 50,000 hrs | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
4 | LED Task Lighting/Screw-in (replacing incandescent lights) | 100 W incandescent replaced with 11 W LED | Indoor Lighting - C | [8 empty] | Yes |  | 5.1699 | 0.90012 | 5.7436 | 5.323 | Yes | 48906.23 | 17.0782 | GPC EnerSim model | 174 fixtures in facility | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 10440 | LED Dimmable 100-120W Replacement Bulb. Extreme Brightness Color: Warm White http://www.amazon.com/Dimmable-100-120W-Replacement-Extreme-Brightness/dp/B002SL4QVI/ref=pd_cp_hi_4 | 66985.3382 | 26 | DEER EUL_Summary_10-1-08 trending to 30,000 hrs | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -182.29 | 0 | Medium
5 | LED Refrigerated Case Door Lighting | LED case lighting in lieu of T-8 lighting | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.67007 | 0.78264 | 0.85617 | 0.69455 | No
6 | Energy Star Battery Charging System (for small cordless products) | On average, use 35% less energy than conventional models | Miscellaneous - C | [8 empty] | Yes |  | 14.7884 | 0.70834 | 20.8776 | 15.3347 | Yes | 12668.47 | 2.4853 | GPC EnerSim model | On average, use 35% less energy than conventional models | Office | Amusement, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 0 | http://www.amazon.com/Duracell-CEF20NC-NIMH-Rechargeable-Charger/dp/B000UKZQ1I | 3298.6771 | 5 | http://articles.cnn.com/2007-10-09/living/rs.rx.electronic_1_preventive-medicine-ipod-battery/2?_s=PM:LIVING, copied dvd player | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -54.77 | 0 | LO_Medium
7 | Window Film | Reduces heat gain to the space by filtering out more solar energy than transparent glass alone. | Cooling - C | [8 empty] | Yes |  | 1.8018 | 0.79996 | 2.2524 | 1.8531 | Yes | 7785.44 | 4.0892 | GPC EnerSim model | Reduced tranmittance from 81% to 33%, 802 sq ft of windows | Lodging | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 3689 | Change per square foot: GILA 48"W x 180"L Heat Blocking Window Film http://www.lowes.com/pd_44606-74130-LES481_0__?productId=1183687&Ntt=window+film&pl=1&currentURL=%2Fpl__0__s%3FNtt%3Dwindow%2Bfilm | 6647.0087 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Fast
8 | Timer for recirculation pump | reduce usage of recirculation pump | Water Heating | [8 empty] | Yes |  | 11.3834 | 0.86714 | 13.1275 | 11.873 | Yes | 3051.95 | 0 | GPC EnerSim model | 1 unit | Lodging | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 106 | Change is from http://www.grainger.com/Grainger/LAING-THERMOTECH-Circulation-Pump-5JKH5?cm_mmc=GoogleBase-_-Pumps-_-Pump%20Controls-_-5JKH5&ci_src=14110944&ci_sku=5JKH5 | 1206.6402 | 11 | DEER EUL_Summary_10-1-08, copied "time clocks" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
9 | Dehumidification system | Reduces load on central cooling coil | Cooling - C | [8 empty] | Yes |  | 0.0098237 | 0.47439 | 0.020708 | 0.01012 | No
10 | Hotels - lighting smart sensor | shuts down lighting in room when swiped with key card as occupant leaves | Interior Lighting - C | [8 empty] | Yes |  | 0.67554 | 0.69667 | 0.96966 | 0.69708 | No
11 | LED exterior lighting | 10 W LED in lieu of 50 W halogen. | Exterior Lighting | [8 empty] | Yes |  | 11.815 | 0.91883 | 12.8588 | 12.2579 | Yes | 101791.8 | 0 | GPC EnerSim model | 287 fixtures | Retail Large | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 7887 | 10 Watt LED Waterpoof Outdoor Security Floodlight 85-264V AC, 3701WH http://www.amazon.com/Waterpoof-Outdoor-Security-Floodlight-85-264V/dp/B004DDQK0O/ref=pd_cp_hi_1 | 93184.9435 | 26 | DEER EUL_Summary_10-1-08 trending to 30,000 hrs | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
12 | cold cathode screw-in bulb | 5 W CCFL replacing 30 W incandescent. | Exterior Lighting | [8 empty] | Yes |  | 5.9313 | 0.90097 | 6.5833 | 6.1179 | Yes | 146614.5 | 35.3987 | GPC EnerSim model | 516 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 5747 | TCP 80089 - 8TFC05F Cold Cathode Screw Base Compact Fluorescent Light Bulb http://www.amazon.com/TCP-80089-8TFC05F-Cathode-Fluorescent/dp/B000R88RN2/ref=sr_1_1?s=hi&ie=UTF8&qid=1316182583&sr=1-1 Requires additional addapter to fit into a standard incandescent. | 127744.3112 | 16 | DEER EUL_Summary_10-1-08 same as CFL fixture | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -1527.87 | 0 | Medium
13 | Elevators | Elevator with high efficiency motor. | Miscellaneous - C | [8 empty] | Yes |  | 2.8121 | 0.8181 | 3.4374 | 2.8976 | Yes | 3612.59 | 1.035 | GPC EnerSim model | six 6 HP motors | Office | Amusement, Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Warehouse | 1228 | Leeson Compressor-Duty Electric Motor - 7.5 HP, 1750 RPM, Model# 140155.00 http://www.amazon.com/Leeson-Compressor-Duty-Electric-Motor-140155-00/dp/B004HL5X0A | 3453.3101 | 15 | DEER EUL_Summary_10-1-08, copied "supply fan motor" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
14 | Ozone commercial laundry system | 70-80% DHW reduction, avg water savings is 25%, & 20-25% reduction in detergent. | Miscellaneous - C | [8 empty] | Yes |  | 2.7401 | 0.63046 | 2.8269 | 2.7456 | Yes | 3276.64 | 0.39 | GPC EnerSim model | 1- 3kW base, chg 2-kw and reduction in hot water | Hospital | Hospital, Lodging, | 12000 | Laundry Systems of Tennessee 865-453-9972 $12,000 for their smallest system | 32881.047 | 11 | DEER EUL_Summary_10-1-08 copied Clothes Washer | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 1417.5 | 341275 | LO_Medium
15 | Data Center - Server/Storage consolidation |  | Cooling, Miscellaneous | [8 empty] | Yes |  | 8.6786 | 0.65681 | 13.2133 | 8.9916 | Yes | 2424267.9 | 559.3493 | GPC EnerSim model | kW reduction from 1547 to 910 (approx 38% savings from reduction in servers) | Data Center | Amusement, Data Center, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 82050 | Nexant program experience/professional judgement | 712078.9477 | 5 | http://www.techrepublic.com/forum/questions/101-331521 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
16 | Data Center - Server/Storage virtualization |  | Cooling, Miscellaneous | [8 empty] | Yes |  | 9.6429 | 0.65681 | 14.6814 | 9.9906 | Yes | 2424267.9 | 559.3493 | GPC EnerSim model | kW reduction from 1547 to 910 (approx 38% savings from reduction in servers) | Data Center | Amusement, Data Center, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 73845 | Nexant program experience/professional judgement | 712078.9477 | 5 | http://www.techrepublic.com/forum/questions/101-331521 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
17 | Data Center - Energy efficient servers |  | Cooling, Miscellaneous | [8 empty] | Yes |  | 2.916 | 0.69953 | 4.1685 | 3.023 | Yes | 104485.59 | 21.8044 | GPC EnerSim model | savings based on % improvement per server and estimated annual operation | Office | Amusement, Data Center, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 8000 | Nexant program experience/professional judgement | 27309.1302 | 5 | http://www.techrepublic.com/forum/questions/101-331521 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -475.69 | 0 | LO_Medium
18 | Data Center - Energy efficient design (even loading on servers, HVAC system) | 20% reduction in kWh for mainframe due mainly to decreased usage on nights and weekends. | Cooling, Miscellaneous | [8 empty] | Yes |  | 9.8811 | 0.75039 | 13.1679 | 10.2885 | Yes | 1078368.72 | 68.5419 | GPC EnerSim model |  | Data Center | Data Center, | 25000 | Nexant program experience/professional judgement | 247027.7632 | 5 | http://www.techrepublic.com/forum/questions/101-331521 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
19 | Clothes Dryer - Heat Pump | equipment replacement | Miscellaneous - C | [8 empty] | No | still in developmental stage | bar: Qualitative Screening 1; Qualitative Screening 4
20 | Clothes Dryer - Microwave | equipment replacement | Miscellaneous - C | [8 empty] | No | still in developmental stage | bar: Qualitative Screening 1; Qualitative Screening 4
21 | Clothes Dryer - Moisture Sensor | most, if not all, dryers now have moisture sensors built in. ENERGY STAR does not rate dryers - their website states that "ENERGY STAR does not label clothes dryers since there is little difference in the energy use between models." | Miscellaneous - C | [8 empty] | No | Standard practice for new dryers | bar: Qualitative Screening 2
22 | Clothes dryer-High Efficiency Motor |  | Miscellaneous - C | [8 empty] | No | Limited market of customers that will be replacing motors in clothes dryers rather than purchasing new one | bar: Qualitative Screening 5
23 | Clothes Washer - Energy Star | (from Energy Star website) this unit uses 50% less energy than standard | Miscellaneous - C | [8 empty] | Yes |  | 21.1716 | 0.46165 | 25.1873 | 21.299 | Yes | 1638.33 | 0.195 | GPC EnerSim model | 1 unit | Hospital | Education, Hospital, Lodging, Restaurant, | 258 | Deemed savings from State trade resource manual | 5462.277 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 208.42 | 50187.5 | LO_Medium
24 | Clothes Washer - CEE Tier 2 or Tier 3 | higher efficiency standards than ES | Miscellaneous - C | [8 empty] | No | Deleted due to overlap with Clothes Washer - Energy Star
25 | High Efficiency Ice Makers - Energy Star | 15% more efficient than standard (and use 10% less water) | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.38863 | 1.0615 | 0.3661 | 0.40361 | No
26 | Energy Star Personal Computer (desktop or laptop) | in sleep mode, uses 4 watts or less | Office Equipment | [8 empty] | No | Standard Practice in Marketplace | bar: Qualitative Screening 2
27 | Energy Star External Power Adapter | On average, 30 percent more efficient than conventional models | Office Equipment | [8 empty] | Yes |  | 6.6116 | 0.6847 | 9.6563 | 6.855 | Yes | 17260.04 | 3.477 | GPC EnerSim model | 20 units | Office | Amusement, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 400 | Engineering judgement: (20) adapters total [2/floor] $20 incremental cost total; Energy star discontinued rating External power adapters December 31, 2010 | 4508.2421 | 5 | http://articles.cnn.com/2007-10-09/living/rs.rx.electronic_1_preventive-medicine-ipod-battery/2?_s=PM:LIVING, copied dvd player | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -76.03 | 0 | LO_Medium
28 | Energy Star Mailing Machine | On average, 25% more efficient than conventional models | Office Equipment | [8 empty] | No | Standard Practice in Marketplace(Combined with other measures into #287) | bar: Qualitative Screening 1
29 | Energy Star Monitor | In sleep mode, uses 2 watts or less. In off mode, uses 1 watt or less | Office Equipment | [8 empty] | No | Standard Practice in Marketplace | bar: Qualitative Screening 2
30 | Energy Star Multifunction Device | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Office Equipment | [8 empty] | No | (Combined with other measures into #287)
31 | Energy Star Scanner | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Office Equipment | [8 empty] | No | (Combined with other measures into #287)
32 | Energy Star Water Cooler | use about half the energy of conventional units | Office Equipment | [8 empty] | Yes |  | 0.62364 | 0.29222 | 2.1342 | 0.64391 | No
33 | High Eff Computer Printers (Energy Star) | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Office Equipment | [8 empty] | No | (Combined with other measures into #287)
34 | High Eff copiers (Energy Star) | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Office Equipment | [8 empty] | No | Standard practice (Combined with other measures into #287) | bar: Qualitative Screening 1
35 | High Eff Fax Machine (Energy Star) | "sleep" or power down when not in use, and use 25% less electricity compared to standard models when on | Office Equipment | [8 empty] | No | Standard practice (Combined with other measures into #287) | bar: Qualitative Screening 1
36 | Plug load sensors | These devises use a motion sensor that is incorporated with a plug load surge suppressor. Inactive equipment can be shut down when the cubicle/office is unoccupied. | Office Equipment | [8 empty] | Yes |  | 1.6371 | 0.75975 | 2.1547 | 1.6944 | Yes | 29787.83 | 6.0428 | GPC EnerSim model | 90 units | Office | Amusement, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 7302 | http://www.wattstopper.com/Commercial-74-122/ISOLE.html 1/1500 sq ft. | 12543.8209 | 8 | DEER EUL_Summary_10-1-08, copied "occupancy sensor" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -134.79 | 0 | LO_Medium
37 | High efficiency ventilation hoods | New "smart" hoods use a series of sensors to set themselves according to your kitchen's needs | Cooking | [8 empty] | Yes |  | 4.1211 | 0.80821 | 5.0991 | 4.2558 | Yes | 4376.54 | 0.96315 | GPC EnerSim model | 3.73kw-2.984kw, no cfm change | Retail Large | Education, Government, Grocery, Hospital, Medical Office, Office, Religious, Large Retail, Small Office, Small Retail, | 779 | RSMeans 233813102970 | 3239.871 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -0.96 | 0 | LO_Medium
38 | Connectionless (Boilerless) Steamers | replacing existing electric steamer | Cooking | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 3.2479 | 0.60852 | 5.3373 | 3.3579 | Yes | 2722.24 | 0.4 | GPC EnerSim model | 1 unit | Restaurant | Education, Grocery, Hospital, Restaurant, | 601 | http://www.cleandishes.com/Product.aspx?productID=118390 | 1951.9841 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
39 | Commercial Hot Food Holding Cabinets (Energy Star) | 60% more energy-efficient than standard models | Cooking | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 1.7338 | 0.66796 | 2.5956 | 1.7915 | Yes | 6255.36 | 1.152 | GPC EnerSim model | 1 unit | Restaurant | Education, Grocery, Hospital, Restaurant, | 2625 | http://www.deiequipment.com/s.nl/it.A/id.4100/.f | 4551.101 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
40 | Commercial Solid Door Refrigerator & Freezer (Energy Star) | ENERGY STAR labeled commercial refrigerators and freezers are more energy efficient because they are designed with components such as ECM evaporator and condenser fan motors, hot gas anti-sweat heaters, or high-efficiency compressors, which will significantly reduce energy consumption and utility bills. | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 33.7615 | 0.83034 | 40.6597 | 34.9399 | Yes | 49532.72 | 7.735 | GPC EnerSim model | 1 unit | Grocery | Amusement, Amusement, Education, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 917 | http://www.centralrestaurant.com/Reach-In-Refrigerator---Standard-Finish-Two-Doors-49-Cu-Ft-c98p3244.html | 30959.3009 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
41 | Commercial Steam Cookers (Energy Star) | up to 60% more energy-efficient than standard models | Cooking | [8 empty] | Yes |  | 3.2479 | 0.60852 | 5.3373 | 3.3579 | Yes | 2722.24 | 0.4 | GPC EnerSim model | 1 unit | Restaurant | Education, Grocery, Hospital, Restaurant, | 601 | http://www.cleandishes.com/Product.aspx?productID=118390 | 1951.9841 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
42 | Refrigerated Beverage Vending Machine (Energy Star) | 35% more energy-efficient than standard new machine models | Refrigeration | [8 empty] | Yes |  | 13.6266 | 0.65098 | 20.9325 | 14.1126 | Yes | 7750.42 | 1.2103 | GPC EnerSim model | kW reduction from 2.73 to 1.35, 2 units | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 298 | RSMeans Online 114113201000 * 10% | 4060.7173 | 10 | DEER EUL_Summary_10-1-08 copied ice machine | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
43 | Vendor Miser | Vending Miser controls save energy by turning off display lights on unrefrigerated machines. Machines are turned off when a passive infrared occupancy sensor registers no occupancy for 15 minutes. | Miscellaneous - C | [8 empty] | Yes | Included in CA energy programs | 12.5297 | 0.75587 | 16.5766 | 12.9877 | Yes | 6992.86 | 1.092 | GPC EnerSim model | 1 unit | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 234 | http://store.usatech.com/vendingmisers.aspx | 2931.955 | 8 | DEER EUL_Summary_10-1-08 copied ltg ctrl | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
44 | High-Efficiency Convection Oven | Heated air is continuously circulated around the food being cooked for more even heat distribution. Temp and cooking times will decrease. On avg, the use of a convection oven will save about a third on energy use. | Cooking | [8 empty] | No | current practice | bar: Qualitative Screening 1 to Qualitative Screening 2
45 | High efficiency fryers (Energy Star) | base case is std electric fryer (for gas to electric conversion, incremental cost is $0) | Cooking | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 1.0443 | 0.76953 | 1.357 | 1.0786 | Yes | 4029.57 | 0.64273 | GPC EnerSim model | 1 unit | Restaurant | Education, Grocery, Hospital, Restaurant, | 2835 | http://www.centralrestaurant.com/0-lb-Oil-Capacity-High-Efficiency-Electric-Fryer-c103p4811.html | 2960.5291 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -0.12 | 0 | LO_Medium
46 | High efficiency griddle | Thermostatic Control Electric Griddle | Cooking | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.76674 | 0.60791 | 1.2613 | 0.79251 | No
47 | Solid-state temperature controls | Solid-state thermostats offer more precise temperature control than conventional ones | Cooking | [8 empty] | Yes |  | 5.7995 | 0.80041 | 7.2456 | 5.9934 | Yes | 9028.6 | 1.59 | GPC EnerSim model | 12 units | Restaurant | Education, Grocery, Hospital, Restaurant, | 1128 | Honeywell T7079B1036 Solid State Remote Thermostat http://www.google.com/products/catalog?num=100&hl=en&biw=1440&bih=753&gs_upl=241079l241079l0l242413l1l1l0l0l0l0l153l153l0.1l1l0&q=Solid-state+temperature+controls&um=1&ie=UTF-8&tbm=shop&cid=4039090777666022393&sa=X&ei=EVigTpyeDImutweZ2IWpBQ&ved=0CGUQ8wIwAQ | 6541.7884 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
48 | High efficiency induction cooking | bottom of pot/pan heated by induction instead of conduction | Cooking | [8 empty] | Yes |  | 2.0841 | 0.62287 | 3.3459 | 2.1555 | Yes | 3311.28 | 0.714 | GPC EnerSim model | 8 units | Restaurant | Education, Grocery, Hospital, Restaurant, | 919 | http://www.centralrestaurant.com/Induction-Range-c181p21079.html | 1915.2697 | 10 | http://log-homes.thefuntimesguide.com/2007/03/life_expectancy_of_homes.php | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
49 | High Efficiency Heat Pump - Air Cooled 11.5 EER 3.2 COP | for heat pumps 65,000 Btu/h - 135,000 Btu/h, 135,000 Btu/h - 250,000 Btu/h | Cooling, Heating - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 2.3463 | 0.61313 | 3.8267 | 2.4112 | Yes | 57368.01 | 23.4894 | GPC EnerSim model | 245 tons cooling | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 28521 | RS Means Online | 66917.6204 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
50 | High Efficiency Heat Pump - Air Cooled 14 SEER | for heat pumps <65,000 Btu/h (3 phase) | Cooling - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 1.5642 | 0.61313 | 2.5511 | 1.6074 | Yes | 57368.01 | 23.4894 | GPC EnerSim model | 245 tons cooling | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 42782 | RS Means Online | 66917.6204 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
51 | High Efficiency Heat Pump - Air Cooled 11.5 EER 3.2 COP | for heat pumps 135,000 Btu/h - 250,000 Btu/h | Cooling, Heating - C | [8 empty] | Yes* | Program currently in place. Duplicate measure (#49)
52 | High Efficiency ASD Chiller | High Efficiency Chiller with lower IPLV (kW/ton) (Water Cooled) | Cooling - C | [8 empty] | Yes |  | 8.7567 | 0.78785 | 11.1147 | 8.9923 | Yes | 89039.03 | 41.4676 | GPC EnerSim model | one 500 ton chiller | Office | Data Center, Government, Hospital, Office, Religious, | 14855 | RSMeans online 500 ton centrifugal chiller plus 7% | 130081.4551 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
53 | High Efficiency Packaged AC - Air Cooled 11.5 EER | for AC units 135,000 Btu/h - 250,000 Btu/h | Cooling - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 3.541 | 2.0565 | 1.7219 | 3.6398 | Yes | 55810.84 | 22.8562 | GPC EnerSim model | (3) 5 tons; (23) 10 tons | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 18564 | RS Means Online | 65735.4852 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
54 | High Efficiency Packaged AC - Air Cooled 11.0 EER | for AC units 65,000 Btu/h - 135,000 Btu/h | Cooling - C | [8 empty] | Yes |  | 5.4561 | 0.67102 | 8.131 | 5.6129 | Yes | 38762.75 | 14.3726 | GPC EnerSim model | (2) 52 tons each | Small Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 7883 | RS Means Online | 43010.2597 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
55 | High Efficiency Packaged AC - Air Cooled 14.0 SEER | for AC units <65,000 Btu/h (3 phase) | Cooling - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 2.3608 | 2.0565 | 1.148 | 2.4266 | Yes | 55810.84 | 22.8562 | GPC EnerSim model | (3) 5 tons; (23) 10 tons | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 27845 | RS Means Online | 65735.4852 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
56 | Heat-Recovery Absorption Chiller |  | Cooling - C | [8 empty] | No | effective if there is existing source of waste heat - so there may be limited applicability. Also difficult to quantify savings due to the varying quantity and temperature of available waste heat. | bar: Qualitative Screening 1; Qualitative Screening 5
57 | High Efficiency Chiller (air cooled) | Next tier above code | Cooling - C | [8 empty] | Yes |  | 6.9417 | 1.0058 | 6.9015 | 7.1479 | Yes | 78991.06 | 25.4019 | GPC EnerSim model | one 500 ton chiller | Office | Data Center, Government, Hospital, Office, Religious, | 14855 | RSMeans online 500 ton centrifugal chiller plus 7% | 103119.1989 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
58 | High Efficiency Chiller (water cooled) | Next tier above code | Cooling - C | [8 empty] | Yes |  | 18.1119 | 0.7948 | 22.788 | 18.6058 | Yes | 186757.55 | 83.5725 | GPC EnerSim model | one 500 ton chiller | Office | Data Center, Government, Hospital, Office, Religious, | 14855 | RSMeans online 500 ton centrifugal chiller plus 7% | 269052.0773 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
59 | Chilled Water Reset, Optimizer System for Chiller(s) | Assume efficiency improvements of 5% | Cooling - C | [8 empty] | Yes |  | 7.3633 | 0.75429 | 9.762 | 7.6 | Yes | 126806.93 | 34.8374 | GPC EnerSim model | efficiency improvement of 5% | Data Center | Data Center, Government, Hospital, Office, Religious, | 10880 | RSMeans Online (labor costs) | 80113.1504 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
60 | Chiller Early Retirement | Replace code compliant chiller from 10 yrs ago with current code compliant chiller. | Cooling - C | [8 empty] | Yes |  | 0.71941 | 0.7849 | 0.91657 | 0.73877 | No
61 | Chiller Tune Up / Diagnostics | Assume efficiency improvements of 5% | Cooling - C | [8 empty] | Yes |  | 50.4463 | 0.78053 | 64.6308 | 52.07 | Yes | 138846.9 | 38.0214 | GPC EnerSim model | (1) 660 ton chiller and (1) 150 ton chiller | Data Center | Data Center, Government, Hospital, Office, Religious, | 1750 | RS Means Online (labor costs) | 88281.0847 | 10 | DEER EUL_Summary_10-1-08 copied refrigerant charge and duct sealing | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Fast
62 | Cooling Tower Optimization | Assume efficiency improvements of 5% | Cooling - C | [8 empty] | Yes |  | 7.7659 | 0.78633 | 9.8762 | 8.0222 | Yes | 113991.82 | 27.6702 | GPC EnerSim model |  | Data Center | Amusement, Data Center, Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 8928 | RS Means Online (labor costs) | 69334.1932 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
63 | Hydronic Economizer | Waterside Economizer b/t CW and CHW loops | Cooling - C | [8 empty] | Yes |  | 0.92204 | 0.77858 | 1.1843 | 0.94683 | No
64 | Outside Air Economizer | Airside economizer | Cooling - C | [8 empty] | Yes |  | 3.92 | 1.4059 | 2.7883 | 4.1814 | Yes | 10848.61 | -1.7252 | GPC EnerSim model | 2,624cfm | Small Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 546 | RSMeans Enthalpy Program, 230923.108180, ~4500~4600~4703 | 2140.3027 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0.04 | 0 | LO_Medium
65 | Hi Eff HVAC System Design | Targeted 15% savings on HVAC savings | Cooling, Heating - C | [8 empty] | Yes |  | 1.0749 | 0.72787 | 1.4768 | 1.1073 | Yes | 109142.21 | 42.7889 | GPC EnerSim model | 3% of building cost targeting 15% HVAC savings | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 75000 | RSMeans Online | 80618.5824 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
66 | High Eff. Ventilation System Design | Targeted 15% in OA energy savings | Cooling - C | [8 empty] | Yes |  | 1.9607 | 0.81134 | 2.4167 | 2.0248 | Yes | 18388.33 | 4.0794 | GPC EnerSim model | targeted 15% in OA energy savings | Small Office | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 6000 | Engineering fees min 4.1% max 10.1 used RS Means new construction calculator and difference between 4.1% design fee and 8.1% design fee | 11764.4661 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
67 | By Pass Timer | takes advantage of free cooling | Cooling - C | [8 empty] | No | economizer is better measure | bar: Qualitative Screening 3
68 | Energy Management System | Whole building automation controls (ltg and HVAC) | Cooling - C | [8 empty] | Yes |  | 1.5532 | 1.2966 | 1.1979 | 1.6054 | Yes | 129127.5 | 30.1572 | GPC EnerSim model | system to control (26) RTUs; 75,621 sq. ft. | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 67736 | RSMeans Online | 115059.5739 | 20 | DEER EUL_Summary_10-1-08, copied "High Efficiency Chillers" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -1222.13 | 0 | Slow
69 | Reduction/Optimization in Fan Flowrate | lower fan flow rates | Cooling, Heating - C | [8 empty] | Yes |  | 1.0517 | 0.81028 | 1.2979 | 1.0897 | Yes | 22898.83 | 3.3167 | GPC EnerSim model | 23-22kW | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 11343 | Nexant Engineering Judgement | 11929.1314 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
70 | Reduction/Optimization of Outside Air Ventilation | demand controlled ventilation | Cooling, Heating - C | [8 empty] | Yes |  | 4.5985 | 0.60375 | 7.6165 | 4.7626 | Yes | 94295.12 | 14.6266 | GPC EnerSim model | 12,921cfm when occupied | Retail Large | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 11343 | Nexant Engineering Judgement | 52160.3554 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
71 | demand controlled ventilation | senses CO2 in return air and adjusts based on occupancy | Cooling, Heating - C | [8 empty] | Yes |  | 1.5363 | 0.67231 | 2.2851 | 1.5953 | Yes | 93831.48 | 11.0593 | GPC EnerSim model | 120 zones | Office | Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Small Office, Small Retail, | 31300 | aSense Wall Ventostat (0-2000ppm CO2 & Temp) http://www.co2meter.com/products/asense-wall-co2-and-temperature-transmitter 8 hours engineer ($200/hr) for programing DCV into EMS | 48085.4308 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
72 | CO sensors for parking garage exhaust fans | sensor control verses timer control | Cooling - C | [8 empty] | Yes |  | 6.3817 | 0.92915 | 6.8683 | 6.6559 | Yes | 32055 | 0 | GPC EnerSim model | 10 sensors | Office | Government, Hospital, Office, Large Retail, | 1677 | Assumed 100k SF parking garage with 1 sensor/ 200 SF RS Means 28314958710 $87.69/sensor and $45 labor / sensor | 10702.0963 | 8 | DEER EUL_Summary_10-1-08, copied "occupancy sensor" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
73 | Indirect/direct air cooling (IDAC - 2 stage Evap system) |  | Cooling - C | [8 empty] | No | Not good applicability due to GA's high wet bulb temps (high humidity) | bar: Qualitative Screening 4; Qualitative Screening 6
74 | Evaporative Pre-Cooler |  | Cooling - C | [8 empty] | No | may not be very effective in GA's humid climate | bar: Qualitative Screening 4; Qualitative Screening 6
75 | High Efficiency Heat Pump - Water Cooled 14 EER 4.6 COP | WSHP system with boiler, cooling tower, pumps, etc. | Cooling - C | [8 empty] | Yes |  | 2.2875 | 0.64002 | 2.994 | 2.3241 | Yes | 43534.11 | 14.1752 | GPC EnerSim model | 17-50 ton WSHP system with boiler, cooling tower, pumps, etc. | Retail Large | Amusement, Data Center, Education, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 35901 | RS Means Online | 82122.0783 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 3132.26 | 0 | LO_Medium
76 | Fan Motor - correct sizing | Installing smaller fan that runs at full load vs large fan that runs less efficiently at part load | Cooling, Heating - C | [8 empty] | Yes |  | 6.7338 | 1.1399 | 5.9072 | 6.9745 | Yes | 5220.72 | 0.68526 | GPC EnerSim model | (2) 12 HP | Small Office | Data Center, Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Small Office, Small Retail, | 0 | RS Means Online | 3213.3787 | 15 | DEER EUL_Summary_10-1-08, copied "High Efficiency Air Conditioner (package and split systems)" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -47.41 | 0 | LO_Medium
77 | Premium Efficient Motor (5hp) |  | Cooling - C | [8 empty] | No | NEMA Prem Eff is now federal code | bar: Qualitative Screening 2
78 | Facility Commissioning | Assume efficiency improvements of 5% | Cooling, Heating - C | [8 empty] | Yes |  | 3.4453 | 0.75319 | 4.5743 | 3.5538 | Yes | 250171.02 | 80.8486 | GPC EnerSim model | 156250 sq ft facility | Office | Data Center, Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Small Office, Small Retail, | 46875 | $0.30 From http://www1.eere.energy.gov/femp/pdfs/OM_7.pdf for median commissioning cost | 161498.5634 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
79 | Destratification Fans |  | Cooling, Heating - C | [8 empty] | No | Difficult to quantify savings - depends on facility size and number of fans installed; difficult to model | bar: Qualitative Screening 1; Qualitative Screening 5
80 | Large Commercial Building Re-Commissioning | Assume efficiency improvements of 5% | Cooling, Exterior Lighting, Heating, Interior Lighting, Refrigeration, Water Heating | [8 empty] | Yes |  | 2.1014 | 0.61336 | 3.4261 | 2.1747 | Yes | 83827.7 | 15.0594 | GPC EnerSim model | 75,621 sq. ft. | Retail Large | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 22686 | Nexant RCx program experience | 47673.431 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
81 | Time Clock |  | Cooling, Heating - C | [8 empty] | No | programmable thermostat or EMS is better measure | bar: Qualitative Screening 3
82 | Room/PTAC AC Energy Star | Energy Star level is 10% greater than federal std - varies from EER of 9.4 to 10.8 depending on unit size | Cooling - C | [8 empty] | Yes |  | 1.1837 | 0.67372 | 1.7569 | 1.2167 | Yes | 17474.0277 | 6.4791 | GPC EnerSim model | 104 tons cooling | Lodging | Lodging | 16380 | 2008 DEER | 19388.7842 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
83 | Appropriately sized rooftop HVAC | Energy Star website estimates that 25% of rooftop HVAC units are oversized | Cooling, Heating - C | [8 empty] | No | Code requirement
84 | HVAC Diagnostic/Air Conditioner Tune Up | 5% efficiency gain | Cooling - C | [8 empty] | Yes |  | 53.6356 | 0.75176 | 71.3469 | 55.5503 | Yes | 78147.78 | 10.648 | GPC EnerSim model | (2) 52 tons each | Small Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 768 | RSMeans Online | 41192.1763 | 10 | DEER EUL_Summary_10-1-08, copied "retrocommissioning" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
85 | HVAC Diagnostic/Heat Pump Tune Up | 5% efficiency gain | Cooling, Heating - C | [8 empty] | Yes |  | 19.8477 | 0.74778 | 23.074 | 20.1272 | Yes | 12381.76 | 5.4673 | GPC EnerSim model | (2) 52 tons each | Small Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 1080 | RSMeans Online | 21435.5137 | 10 | DEER EUL_Summary_10-1-08 copied refrigerant charge and duct sealing | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 1322.12 | 0 | Medium
86 | Improved Equipment Maintenance |  | Cooling, Heating - C | [8 empty] | No | Difficult to determine baseline and expected savings from changes in maintenance plan/schedule | bar: Qualitative Screening 1
87 | Bypass/Delay Timer Direct Expansion |  | Cooling, Heating - C | [8 empty] | No | Difficult to quantify savings - depends on baseline set-up and adjustments made | bar: Qualitative Screening 1
88 | Set-Back Programmable Thermostat | programmable t'stat | Cooling, Heating - C | [8 empty] | Yes |  | 49.3664 | 3.2619 | 15.1343 | 51.3432 | Yes | 14530.61 | 2.9597 | GPC EnerSim model | Manual Heat/Cool Thermostat | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 365 | RSMeans Mechanical Page 267, 1 set back, electric, timed Thermostat | 18018.7263 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
89 | Full Thermal Energy Storage | TES sized to meet entire load | Cooling - C | [8 empty] | Yes |  | 9.6344 | 1.9151 | 5.0309 | 9.8442 | Yes | 186762.1602 | 336.9047 | GPC EnerSim model | TES sized to meet entire load {Used 6,000 Hour BASE model, moved compressor load for 4 units from 14-19 hour to off peak hour to simulate making ice at night. Ice making hours spread across 10 hour period} | Office | Data Center, Government, Hospital, Office, Religious, | 56350 | Online vendor quote | 542901.2564 | 20 | DEER EUL_Summary_10-1-08, copied "High Efficiency Chillers" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Slow
90 | Partial Thermal Energy Storage | TES sized to meet partial load | Cooling - C | [8 empty] | Yes |  | 24.9926 | 1.3333 | 18.7456 | 25.5549 | Yes | 186759.8535 | 210.2386 | GPC EnerSim model | TES sized to meet partial load {Used 6,000 Hour BASE model, moved compressor load for 4 units from 14-19 hour to off peak hour to simulate making ice at night. Ice making hours spread across 10 hour period} | Office | Data Center, Government, Hospital, Office, Religious, | 16905 | Online vendor quote | 422500.129 | 20 | DEER EUL_Summary_10-1-08, copied "High Efficiency Chillers" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Slow
91 | Air Duct/Water Pipe Insulation |  | Cooling - C | [8 empty] | No | standard practice | bar: Qualitative Screening 2
92 | ASD HVAC Fan | Constant speed fan vs fan with VFD | Cooling, Heating - C | [8 empty] | Yes |  | 2.2256 | 1.0064 | 2.2114 | 2.3054 | Yes | 19210.82 | 2.3357 | GPC EnerSim model | two 20 HP | Small Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 4144 | Local vendor quotes | 11771.8046 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -175.92 | 0 | LO_Medium
93 | Variable Air Volume Control (VSD) |  | Cooling - C | [8 empty] | No | Difficult to quantify savings - depends on facility loads | bar: Qualitative Screening 1
94 | Office Load Control (shed) | Load shedding measure to keep customer in lower tier of rates | Cooling, Exterior Lighting, Heating, Interior Lighting | [8 empty] | Yes |  | 0.5376 | 3.4616 | 0.1553 | 0.54908 | No
95 | Compact Fluorescent Lamp/Hardwire | 14W replacing 60W incandescent | Interior Lighting - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 5.6337 | 0.90517 | 6.2239 | 5.8111 | Yes | 157103.9 | 37.8896 | GPC EnerSim model | 632 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 8047 | Change is equivalent CF (http://www.amazon.com/47448-29-Watt-150-Watt-equivalent-Energy/dp/B000WUEP9U/ref=sr_1_2?ie=UTF8&qid=1311341919&sr=8-2) | 137270.1631 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -1596.1 | 0 | Fast
96 | Compact Fluorescent Lamp/Screw-in | replacing incandescent lamps | Interior Lighting - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 3.8738 | 0.68101 | 5.6882 | 4.0141 | Yes | 157103.9 | 37.8896 | GPC EnerSim model | 632 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 5776 | Change is equivalent CF (http://www.amazon.com/47448-29-Watt-150-Watt-equivalent-Energy/dp/B000WUEP9U/ref=sr_1_2?ie=UTF8&qid=1311341919&sr=8-2) | 42409.9821 | 5 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -1596.1 | 0 | LO_Fast
97 | Task Lighting | can reduce ambient lighting if task lighting is used | Interior Lighting - C | [8 empty] | No | Difficult to quantify savings - difference in lighting from overhead to task lighting | bar: Qualitative Screening 1
98 | Delay Timer |  | Interior Lighting - C | [8 empty] | No | Better measure is Occupancy Sensor (interior lighting): (#122) | bar: Qualitative Screening 2 to Qualitative Screening 3
99 | Elapsed time switch T12 |  | Interior Lighting - C | [8 empty] | No | Difficult to quantify savings - depends on facility schedule and current practices. Better measure is Occupancy Sensor (interior lighting): (#122) | bar: Qualitative Screening 1; Qualitative Screening 3
100 | Elapsed time switch T8 |  | Interior Lighting - C | [8 empty] | No | Difficult to quantify savings - depends on facility schedule and current practices. Better measure is Occupancy Sensor (interior lighting): (#122) | bar: Qualitative Screening 1; Qualitative Screening 3
101 | Install Timers on Exterior Lights |  | Exterior Lighting | [8 empty] | No | better measure is Photocell Controls (outdoor) (#131) | bar: Qualitative Screening 2 to Qualitative Screening 3
102 | Time Clock |  | Exterior Lighting | [8 empty] | Yes | Duplicate of ID# 81
103 | Commercial Lighting Remodeling (Energy effective lighting) |  | Exterior Lighting, Interior Lighting | [8 empty] | No | Difficult to quantify savings - depends on baseline equipment. Savings captured in individual lighting measures | bar: Qualitative Screening 1
104 | Lighting Channels (Tunnels) | series of lights that will be treated as one for the purpose of scene setting | Interior Lighting - C | [8 empty] | No | Only useful if need several different lighting setups for different tasks | bar: Qualitative Screening 4 to Qualitative Screening 5
105 | Reflectors/Delamping | Reducing 4 Lamp over head to either 3 or 2 lamp setting with reflectors. | Interior Lighting - C | [8 empty] | Yes |  | 2.7761 | 0.81229 | 3.4176 | 2.8664 | Yes | 253666.44 | 61.2914 | GPC EnerSim model | 680 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 40800 | Nexant program experience/Engineering Judgement | 155785.3962 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -2620.5 | 0 | Fast
106 | Daytime Dimming |  | Interior Lighting - C | [8 empty] | No | Difficult to quantify savings - depends on building orientation and number of windows | bar: Qualitative Screening 1
107 | Daylighting |  | Interior Lighting - C | [8 empty] | No | Better measure is use of daylight sensors (#108); daylighting measure alone is behavioral change or would be included in new construction design | bar: Qualitative Screening 3
108 | Indoor Daylight Sensors | daylighting | Interior Lighting - C | [8 empty] | Yes |  | 9.9882 | 0.69513 | 14.3687 | 10.308 | Yes | 56543.72 | 18.9149 | GPC EnerSim model | 31 sensors, 15,625 sq ft | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 1493 | http://www.amazon.com/Thomas-Betts-Carlon-Photocell-HS525/dp/B00111C064/ref=sr_1_1?s=hi&ie=UTF8&qid=1312983926&sr=1-1) | 28320.766 | 8 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -217.13 | 0 | LO_Medium
109 | Exit Sign Retrofit: Compact Fluorescent, replacing incandescent | Exit sign with interior compact fluorescent bulb replacing interior incandescent. | Interior Lighting - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 1.2314 | 0.94687 | 1.3005 | 1.2677 | Yes | 4825.52 | 1.7414 | GPC EnerSim model | 12 fixtures | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 3849 | Big Beam 2ECXP1RWW Exit Sign, Fluorescent, 120V, Chicago Code http://www.google.com/products/catalog?hl=en&q=Fluorescent+exit+sign&gs_upl=72602l74852l2l75159l12l12l0l0l0l4l304l2031l4.4.3.1l12l0&um=1&bav=on.2,or.r_gc.r_pw.&biw=1600&bih=753&ie=UTF-8&tbm=shop&cid=5343631830887726314&sa=X&ei=qIV3Tu-1Jsi1twfd8-HmDw&ved=0CF8Q8wIwAA Wiring stays the same, but the canopy must be replaced. | 4792.5078 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -18.43 | 0 | Fast
110 | LED Exit Sign, Replacing Incandescent | Exit sign with interior LED replacing interior incandescent. | Interior Lighting - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 2.2386 | 0.9888 | 2.264 | 2.3051 | Yes | 5789.86 | 2.0828 | GPC EnerSim model | 120 fixtures | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 2415 | Aluminum LED Exit Sign Red Lettering Battery Backup http://www.bulbs.com/espec.aspx?ID=9806&RefId=193 | 5729.6816 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -21.01 | 0 | Fast
111 | Electrodeless Fluorescent | 100 watt T17 Mounting Brackets Base 4,100K 800 Series Electrodeless Icetron with Internal Reflector Ecologic Fluorescent Sylvania Light Bulb | Interior Lighting - C | [8 empty] | Yes |  | 0.92047 | 1.063 | 0.86593 | 0.94906 | No
112 | T8 Lamp/Electronic Ballasts: 4 foot fixture |  | Interior Lighting - C | [8 empty] | No | Changed to T8 lamp (any length) electronic ballast #327
113 | T8 Lamp/Electronic Ballasts: 8 foot fixture |  | Interior Lighting - C | [8 empty] | No | Changed to T8 lamp (any length) electronic ballast #327
114 | T8 Lamp/Electronic Ballasts: other sizes |  | Interior Lighting - C | [8 empty] | No | Changed to T8 lamp (any length) electronic ballast #327
115 | Linear fluorescent electronic ballasts |  | Interior Lighting - C | [8 empty] | No | better measure is converting to T8 Lamp/Electronic Ballasts: (#'s 112-114) | bar: Qualitative Screening 3
116 | Interior High Bay Linear Fluorescent Fixture (T8 or T5 w/reflector) | replacing incandescent, T12, and HID fixtures | Interior Lighting - C | [8 empty] | Yes |  | 2.9905 | 0.7513 | 3.9804 | 3.083 | Yes | 274307.99 | 82.4223 | GPC EnerSim model | 359 fixtures | Warehouse | Amusement, Warehouse | 27614 | High Bay Light Fixture 6 Lamps T8 With Miro 4 Reflector 120-227 Volts http://www.amazon.com/Light-Fixture-Lamps-Reflector-120-227/dp/B003XW4SGY/ref=sr_1_1?s=hi&ie=UTF8&qid=1316195759&sr=1-1 | 160908.7813 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -4307.23 | 0 | LO_Medium
117 | HID Lighting | includes metal halide and HPS | Exterior Lighting, Interior Lighting | [8 empty] | Yes |  | 4.9625 | 0.81554 | 6.0849 | 5.113 | Yes | 137187.86 | 40.0276 | GPC EnerSim model | 220 fixtures | Warehouse | Amusement, Warehouse | 1426 | 100/175 Watt PSMH Eiko 100W Clear ED-17 Pulse Start Med Base (E26) Metal Halide (MH) http://www.google.com/products/catalog?hl=en&sugexp=bvie&cp=20&gs_id=6u&xhr=t&q=100+watt+pulse+start+metal+halide&pq=100+watt++psmh&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&biw=1440&bih=722&um=1&ie=UTF-8&tbm=shop&cid=5580360465573065944&sa=X&ei=w-qNTt2JMcSutwf22MGnDA&sqi=2&ved=0CFAQ8wIwAg | 112707.8427 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -2144.52 | 0 | LO_Medium
118 | HPS Lamps - Street | 100W Clear Pulse Start Med Base | Exterior Lighting | [8 empty] | Yes |  | 2.1842 | 0.88215 | 2.476 | 2.2774 | Yes | 66762.15 | 0 | GPC EnerSim model | 141 fixtures | Office | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 17484 | 100/175 Watt PSMH Eiko 100W Clear ED-17 Pulse Start Med Base (E26) Metal Halide (MH) http://www.google.com/products/catalog?hl=en&sugexp=bvie&cp=20&gs_id=6u&xhr=t&q=100+watt+pulse+start+metal+halide&pq=100+watt++psmh&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&biw=1440&bih=722&um=1&ie=UTF-8&tbm=shop&cid=5580360465573065944&sa=X&ei=w-qNTt2JMcSutwf22MGnDA&sqi=2&ved=0CFAQ8wIwAg | 38187.853 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
119 | Induction Lamps (baseline incandescent or mercury vapor) | 80W induction lamp and ballast replacing 250W incandescent | Interior Lighting - C | [8 empty] | Yes |  | 2.0115 | 0.92351 | 2.1781 | 2.0869 | Yes | 98998.2 | 0 | GPC EnerSim model | 284 fixtures | Retail Large | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 47596 | 80 Watt 80W Circular Round Saturn Series Induction 120 Volt Lamp / Bulb 5000K with Ballast with 5 Year Warranty http://www.shineretrofits.com/outdoor-pole-induction-lighting-retrofit-kits-kumho-econergy-100000-hour-lamp-direct-fit-energy-efficient-hid-hps-replacement/induction-lamp-ballast-retrofit-kit-23w-40w-50w-60w-70w-80w-100w-120w-150w-200w-250w-300w-400w-120v-277v-347v-480v-3?gclid=CKWAqrfS1KsCFQFS7AodqhrYNQ | 95738.1996 | 29 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
120 | ceramic metal halide | replacing incandescent, halogen, or halogen infrared fixtures | Interior Lighting - C | [8 empty] | Yes |  | 2.9446 | 0.81678 | 3.6051 | 3.0328 | Yes | 268320.9 | 81.0998 | GPC EnerSim model | 430 fixtures | Warehouse | Amusement, Warehouse | 39198 | GE 42729 250-Watt Multi-Vapor Quartz Metal Halide Mogul Light Bulb, 1-Pack http://www.amazon.com/42729-250-Watt-Multi-Vapor-Quartz-Halide/dp/B00076IMYI/ref=sr_1_6?s=hi&ie=UTF8&qid=1319566464&sr=1-6 | 212286.6717 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -4213.85 | 0 | Medium
121 | Interior Metal Halide Pulse Start Fixtures | replacing standard metal halide | Interior Lighting - C | [8 empty] | Yes |  | 1.4188 | 0.78678 | 1.8033 | 1.4618 | Yes | 268320.9 | 81.0998 | GPC EnerSim model | 922 fixtures | Warehouse | Amusement, Warehouse | 118016 | 70 Watt - ED28 - Pulse Start - Metal Halide - Unprotected Arc Tube - 4200K - Mogul Base - ANSI M98/E - Universal BURN - MH70/ED28/U/4K - Plusrite 1011 http://www.google.com/products/catalog?hl=en&q=70+watt+pulse+start+metal+halide&rlz=1R2ADFA_enUS439&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&biw=1440&bih=640&wrapid=tljp1317924265848021&um=1&ie=UTF-8&tbm=shop&cid=7670208575006523421&sa=X&ei=gPSNToupMpDBtgeG1JWhDA&sqi=2&ved=0CGYQ8wIwAg# | 186028.8437 | 13 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -4213.85 | 0 | Medium
122 | Occupancy Sensor (interior lighting): | Wall mounted, convenient push-button provides manual on/off light switching at any time, 180 degrees field-of-view provides approximately 2100 square feet of coverage, Horizontal field of view may be adjusted between 180 degrees and 32 degrees of arc | Interior Lighting - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 134.645 | 0.33559 | 401.2223 | 138.1287 | Yes | 126009.12 | 100.514 | GPC EnerSim model | 29 fixtures controlled | Hospital | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 717 | Change is (http://www.amazon.com/Leviton-ODS10-ID-Decora-Switch-Occupancy/dp/B0007N72P6/ref=sr_1_2?ie=UTF8&qid=1301581139&sr=8-2) | 96540.4535 | 8 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
123 | Ellipsoidal Reflector Lamps |  | Interior Lighting - C | [8 empty] | No | Current practice. Measure widely used in market place. | bar: Qualitative Screening 2
124 | Halogen Lamp | tungsten halogen | Interior Lighting - C | [8 empty] | Yes |  | 0.077148 | 0.47429 | 0.16266 | 0.080582 | No
125 | Light Pipes | 2 foot long, 10" diameter lighting tube bringing in sunlight from exterior to interior spaces. | Interior Lighting - C | [8 empty] | Yes |  | 1.628 | 0.90198 | 1.8049 | 1.6764 | Yes | 11509.51 | 3.9035 | GPC EnerSim model | 15, 625 sq ft | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 7688 | Natural Light 10" Tubular Skylight 2 ft Light Pipe http://www.google.com/products/catalog?hl=en&cp=11&gs_id=v&xhr=t&q=light+pipes&rlz=1R2ADFA_enUS439&biw=1440&bih=640&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&wrapid=tljp1317931031613020&um=1&ie=UTF-8&tbm=shop&cid=14948783600330580266&sa=X&ei=GwiOTtO7PIi4tgfBkpSpDA&sqi=2&ved=0CG8Q8wIwAQ# assume 1 tube every 500 sq ft of roof area | 13111.2691 | 20 | DEER EUL_Summary_10-1-08 copied roof insulation | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -65.05 | 0 | LO_Medium
126 | Sulfur Lights |  | Interior Lighting - C | [8 empty] | No | Technology is not currently being developed | bar: Qualitative Screening 1; Qualitative Screening 4
127 | T5 Lighting (base T-12) | T-12 replaced with 21 Watt T5 Fluorescent Bulb | Interior Lighting - C | [8 empty] | Yes |  | 2.9512 | 0.8098 | 3.6444 | 3.0473 | Yes | 372232.11 | 90.0338 | GPC EnerSim model | 1410 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 53566 | 21 Watt, 34 Inch T5 Cool White Fluorescent Bulb http://www.bulbs.com/espec.aspx?ID=14263 | 228084.3539 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -3926.48 | 0 | Medium
128 | Refrigerated Case Door Lighting - Electronic Ballasts | One T8 bulb and electronic ballast per refrigerator case door. | Refrigeration | [8 empty] | Yes |  | 19.5581 | 0.8232 | 23.7585 | 20.2542 | Yes | 37854 | 6 | GPC EnerSim model | 25 doors | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Restaurant, Large Retail, Small Retail, | 1092 | GLC-UNV40 Multi-Volt Ballast for one or two F32T8 or F40T8 http://www.refrigerationballast.com/GLC-UNV40-Multi-Volt-Ballast-for-one-or-two-F32T8-or-F40T8-GLC-UNV40.htm | 21357.3979 | 10 | DEER EUL_Summary_10-1-08 copied ice machine | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
129 | Incandescent to HID (outdoor) | 100W HID replacing 250W incandescent | Exterior Lighting | [8 empty] | Yes |  | 3.5417 | 0.69992 | 5.0602 | 3.6735 | Yes | 35312.85 | 0 | GPC EnerSim model | 54 fixtures | Retail Large | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 6696 | 100/175 Watt PSMH Eiko 100W Clear ED-17 Pulse Start Med Base (E26) Metal Halide (MH) http://www.google.com/products/catalog?hl=en&sugexp=bvie&cp=20&gs_id=6u&xhr=t&q=100+watt+pulse+start+metal+halide&pq=100+watt++psmh&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&biw=1440&bih=722&um=1&ie=UTF-8&tbm=shop&cid=5580360465573065944&sa=X&ei=w-qNTt2JMcSutwf22MGnDA&sqi=2&ved=0CFAQ8wIwAg | 23715.4504 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
130 | Mercury Vapor to HID (outdoor) | 100W HID replacing 250W mercury vapor | Exterior Lighting | [8 empty] | Yes |  | 999.99 | 0.67447 | 999.99 | 999.99 | Yes | 46007.1 | 0 | GPC EnerSim model | 54 fixtures | Retail Large | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 0 | 100/175 Watt PSMH Eiko 100W Clear ED-17 Pulse Start Med Base (E26) Metal Halide (MH) http://www.google.com/products/catalog?hl=en&sugexp=bvie&cp=20&gs_id=6u&xhr=t&q=100+watt+pulse+start+metal+halide&pq=100+watt++psmh&gs_upl=&bav=on.2,or.r_gc.r_pw.,cf.osb&biw=1440&bih=722&um=1&ie=UTF-8&tbm=shop&cid=5580360465573065944&sa=X&ei=w-qNTt2JMcSutwf22MGnDA&sqi=2&ved=0CFAQ8wIwAg | 18904.192 | 9 | DEER EUL_Summary_10-1-08 trending to 10,000 hrs | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
131 | Photocell Controls (outdoor) | sensor control verses timer control | Exterior Lighting | [8 empty] | Yes |  | 1.1834 | 0.66417 | 1.7817 | 1.2434 | Yes | 16036 | 0 | GPC EnerSim model | 247 fixtures | Retail Large | Amusement, Data Center, Government, Grocery, Lodging, Office, Restaurant, Large Retail, Small Office, Small Retail, | 2364 | Change is (http://www.amazon.com/Thomas-Betts-Carlon-Photocell-HS525/dp/B00111C064/ref=sr_1_1?s=hi&ie=UTF8&qid=1312983926&sr=1-1) | 2797.4459 | 8 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
132 | LED Traffic Signal | EPACT 2005 set efficiency level for traffic signals to meet the previous Energy Star level - ES no longer qualifies traffic signals | Miscellaneous - I | [8 empty] | No | Current practice. Measure widely used in market place. | bar: Qualitative Screening 2
133 | Low Pressure Drop Pool Filter |  | Miscellaneous - C | [8 empty] | No | Poor customer acceptance due to reduced effectiveness of filtration system | bar: Qualitative Screening 5
134 | Premium Efficient Motors (50 hp): Summary Level |  | Miscellaneous - I | [8 empty] | No | NEMA Prem Eff is now federal code | bar: Qualitative Screening 2
135 | TOD Pool Pump Timer |  | Miscellaneous - C | [8 empty] | No | standard practice for most commercial pools | bar: Qualitative Screening 1
136 | Adjustable Speed Drives (ASD) | VFD on pumps | Miscellaneous - C | [8 empty] | Yes |  | 2.8428 | 1.3818 | 2.0573 | 2.9489 | Yes | 16566.42 | 1.4496 | GPC EnerSim model | Condensor-15kw (2) 7.5 HP, Chill water-15kw (2) 7.5 HP | Office | Amusement, Data Center, Education, Government, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 4640 | Local vendor quotes | 13190.3997 | 15 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
137 | Motor early retirement |  | Miscellaneous - I | [8 empty] | No | Difficult to quantify savings - depends on age and condition of motor | bar: Qualitative Screening 1
138 | Compressed Air System Improvements | improvements can include replacement, leak repair, VSD, increased storage, etc) | Miscellaneous - I | [8 empty] | Yes |  | 1.8588 | 0.85254 | 2.1803 | 1.9418 | Yes | 5445.8 | 0 | GPC EnerSim model |  | Hospital | Hospital, Warehouse | 1076 | Nexant program experience/Engineering Judgement | 2000.0869 | 10 | DEER EUL_Summary_10-1-08, copied "Refrigerant Charge" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
139 | Off Peak Battery Charging | charging during off-peak hours | Miscellaneous - C | [8 empty] | Yes |  | 999.99 | 1.2129 | 999.99 | 999.99 | Yes | 5933.0102 | 3.251 | GPC EnerSim model | 5kw forklift batery charger used. | Warehouse | Warehouse | 0 | N/A (no cost measure) | 1748.6782 | 5 | Nexant judgement | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
140 | Greenhouse Heat Curtain | Thermal curtain is deployed at night to reduce heat required for freeze protection | Heating - C | [8 empty] | Yes |  | 0.44146 | 0.87086 | 0.50693 | 0.46034 | No
141 | Low-Pressure Impact Sprinkler Nozzle: Permanent, Solid-Set | lowers pump run hours and water usage | Miscellaneous - C | [8 empty] | Yes |  | 2.3711 | 1.5044 | 1.5761 | 2.4395 | Yes | 1770.4102 | 2.4252 | GPC EnerSim model | (1) 5hp pump and (50) nozzles | Warehouse | Warehouse | 477 | Cost from online vendor | 1131.6017 | 10 | DEER EUL_Summary_10-1-08, copied "Faucet Aerators" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
142 | Low-Pressure Impact Sprinkler Nozzle: Portable, Hand-Move | lowers pump run hours and water usage | Miscellaneous - C | [8 empty] | Yes |  | 2.3711 | 1.5044 | 1.5761 | 2.4395 | Yes | 1770.4102 | 2.4252 | GPC EnerSim model | (1) 5hp pump and (50) nozzles | Warehouse | Warehouse | 477 | Cost from online vendor | 1131.6017 | 10 | DEER EUL_Summary_10-1-08, copied "Faucet Aerators" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
143 | Pump Repair: impeller & bowls: 100 - 400 hp |  | Miscellaneous - I | [8 empty] | No | Difficult to quantify savings - depends on condition of existing pumps | bar: Qualitative Screening 1
144 | Pump Repair: impeller & bowls: 20 - 75 hp |  | Miscellaneous - C | [8 empty] | No | Difficult to quantify savings - depends on condition of existing pumps | bar: Qualitative Screening 1
145 | Sprinkler Irrigation to Micro Irrigation System: No Well | lowers pump run hours and water usage | Miscellaneous - I | [8 empty] | Yes |  | 0.0079256 | 0.85864 | 0.0092304 | 0.0081353 | No
146 | Sprinkler Irrigation to Micro Irrigation System: Well | lowers pump run hours and water usage | Miscellaneous - I | [8 empty] | Yes |  | 0.016285 | 0.85984 | 0.01894 | 0.016716 | No
147 | Tape drip irrigation | lowers pump run hours and water usage | Miscellaneous - I | [8 empty] | Yes |  | 0.055578 | 0.92505 | 0.060081 | 0.05698 | No
148 | High Efficiency Refrigeration Compressor | Assumed High Eff Compressor to be 15% more eff | Refrigeration | [8 empty] | Yes |  | 29.6457 | 0.79364 | 37.3539 | 30.6859 | Yes | 130125.36 | 19.44 | GPC EnerSim model |  | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 2748 | RSMeans 40 Ton Refrig Compressor, from 89 kW Large storage model breakdown, typical refr COP 1.4, equals approx 35 Tons | 81466.3367 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
149 | Parallel Unequal Compressor Sys. |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system requirements | bar: Qualitative Screening 1
150 | Variable Speed Compressor Systems |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system requirements | bar: Qualitative Screening 1
151 | High Efficiency Glass Doors | Door with higher U-value and SHGC than code | Refrigeration | [8 empty] | Yes |  | 0.45829 | 1.2433 | 0.36861 | 0.47481 | No
152 | Food Service Refrigeration: Cooler/Freezer Door Gaskets | retrofit of existing cooler/freezer doors | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 3.0908 | 0.6204 | 4.982 | 3.2123 | Yes | 11072.02 | 1.729 | GPC EnerSim model | 2.53 kW/door, one gasket/door | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 741 | 2008 DEER | 2290.3105 | 4 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
153 | Auto-Closers for Cooler or Freezer Doors | retrofit of existing cooler/freezer doors | Refrigeration | [8 empty] | Yes |  | 0.13206 | 1.1383 | 0.11601 | 0.13703 | No
154 | Glass or Acrylic Doors: low temperature case | install on upright display cases | Refrigeration | [8 empty] | Yes |  | 0.45829 | 1.2433 | 0.36861 | 0.47481 | No
155 | Strip Curtains | this measure includes both reach-coolers and refrigerated rooms/warehouses | Refrigeration | [8 empty] | Yes |  | 2.1671 | 0.58622 | 3.6966 | 2.2522 | Yes | 4661.91 | 0.728 | GPC EnerSim model | 280 sq ft | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 445 | Online vendor quote | 964.3427 | 4 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
156 | Night Covers for Display Cases |  | Refrigeration | [8 empty] | No | Poor customer acceptance due to increase in labor required to implement | bar: Qualitative Screening 6
157 | Refrigerated Case Doors- Door Miser |  | Refrigeration | [8 empty] | No | Better Measure is Anti-Sweat Heat Control-Humidistat (#165) (door miser is specific brand) | bar: Qualitative Screening 3
158 | Refrigerated Case Special Doors with low/no anti-sweat heat | special door that requires minimum to no anti-sweat heat. | Refrigeration | [8 empty] | Yes |  | 1.2799 | 1.2387 | 1.0333 | 1.326 | Yes | 1460.87 | 0.1764 | GPC EnerSim model | 16 doors | Restaurant | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Restaurant, Large Retail, Small Retail, | 693 | Online vendor quote (Anthony doors) | 886.9823 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
159 | Mechanical Subcoolers |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - energy savings for dual cycle system depend on required facility load | bar: Qualitative Screening 1
160 | High Eff. Evaporator Fan Motors |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on the condition and operation of baseline equipment | bar: Qualitative Screening 1
161 | Electronic Adjustable Speed Drives |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system demand | bar: Qualitative Screening 1
162 | Anti-Sweat Heat Control-Time Clock |  | Refrigeration | [8 empty] | No | Better Measure is Anti-Sweat Heat Control-Humidistat (#165) | bar: Qualitative Screening 3
163 | High Efficiency condenser |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system demand | bar: Qualitative Screening 1
164 | High Efficiency Packaged Refrigeration Equip | assume 15% savings | Refrigeration | [8 empty] | Yes |  | 5.3187 | 0.84723 | 6.2778 | 5.5044 | Yes | 14568.45 | 2.275 | GPC EnerSim model | 1 unit | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 1712 | http://www.bohn.com/products/ProductDetail.aspx?&TabIdx=1&PID=2735&cID=2 | 9105.6762 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
165 | Anti-Sweat Heat Control-Humidistat | heat control dependant on humidistat vs timer or constant | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 7.8342 | 0.8521 | 9.194 | 8.157 | Yes | 98675.81 | 2.357 | GPC EnerSim model | 15 doors on one circuit | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 6214 | 2008 DEER | 48681.8715 | 12 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
166 | Anti-Sweat Heat Control-Time Clock |  | Refrigeration | [8 empty] | No | humidity sensor is better measure | bar: Qualitative Screening 2
167 | Desuperheaters |  | Refrigeration | [8 empty] | No | refrigeration savings are not easy to be quantified - majority of savings for desuperheater are in water heating | bar: Qualitative Screening 1
168 | Economizer for Walk-in Coolers | The economizer constantly monitors exterior air temperature. It automatically draws outside air into the cooler/freezer whenever it is cold enough to substitute for compressor-generated cooling. | Refrigeration | [8 empty] | Yes |  | 19.0065 | 0.79637 | 23.8664 | 19.6844 | Yes | 27388.69 | 4.277 | GPC EnerSim model | Standard Eff 10 HP motor | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 755 | Average of three prices listed for High Eff. Fans at: https://secure.progress-energy.com/businessenergycheck/library/MISC004.asp 1 fan per kW | 14349.8965 | 10 | DEER EUL_Summary_10-1-08 copied heat recovery | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
169 | Evaporate Pre-Cooler |  | Refrigeration | [8 empty] | No | Not good applicability due to GA's high wet bulb temps (high humidity) | bar: Qualitative Screening 4
170 | Evaporator-cooled condenser | replacing air-cooled condenser | Refrigeration | [8 empty] | No | Not good applicability due to GA's high wet bulb temps (high humidity) | bar: Qualitative Screening 1; Qualitative Screening 5
171 | Floating Head Pressure Control |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system demand | bar: Qualitative Screening 1; Qualitative Screening 5
172 | Food Service Refrigeration: Condensate Evaporator | operates on the same principle as a "swamp cooler." | Refrigeration | [8 empty] | No | Not good applicability due to GA's high wet bulb temps (high humidity) | bar: Qualitative Screening 4; Qualitative Screening 6
173 | Refrig. Equip., Defrost Control System |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - savings depend on frequency of use and humidity | bar: Qualitative Screening 1
174 | Refrig: Evaporator Fan Controller |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on system demand, duty cycle, and motor power | bar: Qualitative Screening 1
175 | Insulation for bare suction lines | lines that run from the evaporator to the compressor lose heat to the environment. | Refrigeration | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 12.4559 | 0.81617 | 15.2613 | 12.8945 | Yes | 6992.86 | 1.092 | GPC EnerSim model | 622 ft of pipe | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 323 | http://www.plumbers-supply-co.com/default.aspx?page=item%20detail&itemcode=NL12.13 | 4023.2561 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
176 | Improved Equipment Maintenance |  | Refrigeration | [8 empty] | No | Difficult to quantify savings - depends on age and condition of existing equipment Duplicate of ID# 86 | bar: Qualitative Screening 1
177 | Air curtain technology | A fan placed over a doorway creates a "curtain" of air to maintain the needed pressure to keep temperature controled air inside the space. | Refrigeration | [8 empty] | Yes |  | 8.077 | 0.66006 | 12.2367 | 8.3723 | Yes | 4661.91 | 0.728 | GPC EnerSim model | 1 door | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 242 | http://www.grainger.com/Grainger/MARS-AIR-DOORS-Air-Curtain-2CKU4?Pid=search | 1954.6381 | 8 | DEER EUL_Summary_10-1-08 copied heat recovery | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
178 | Ceiling Insulation | R-30 to R-50 | Cooling - C | [8 empty] | Yes |  | 0.33134 | 3.0116 | 0.28346 | 0.33298 | No
179 | High Efficiency Building Shell Design (Energy Star) | program to gain Energy Star building label | Cooling - C | [8 empty] | No | Difficult to quantify savings - no baseline system for comparison | bar: Qualitative Screening 1
180 | EnergySmart Schools | program through U.S. DOE, similar to Energy Star homes | Cooking, Cooling, Exterior Lighting, Heating, Interior Lighting, Miscellaneous, Office Equipment, Refrigeration, Water Heating | [8 empty] | Yes |  | 0.39649 | 0.86636 | 0.45453 | 0.4073 | No
181 | Light Colored Roofs and Walls/Cool Roofs | more reflective roof | Cooling - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.53897 | 1.3858 | 0.38892 | 0.55752 | No
182 | Awning |  | Cooling - C | [8 empty] | No | Difficult to quantify savings - depends on building orientation and placement of awnings | bar: Qualitative Screening 1
183 | High Efficiency Energy Star Windows & Skylights, 0.40 SHGC | U-value=0.35/SHGC=0.30 base (where appliciable) is U-value=0.50/SHGC=0.30 | Cooling - C | [8 empty] | Yes |  | 3.3626 | 0.70543 | 4.7667 | 3.4624 | Yes | 2130.28 | 0.74153 | GPC EnerSim model | 567 sq ft | Retail Large | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 680 | Price for window is http://www.homedepot.com/Energy-Star/Doors-Windows-Windows-Single-Hung/h_d1/N-5yc1vZas73Z1z141o3Z1z112sv/R-100627485/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053 | 2638.3607 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -10.22 | 0 | LO_Medium
184 | Interior Shade |  | Cooling - C | [8 empty] | No | Difficult to quantify savings - depends on building orientation and number of windows | bar: Qualitative Screening 1
185 | Overglazing |  | Cooling - C | [8 empty] | No | Difficult to quantify savings - depends on building orientation and number of windows | bar: Qualitative Screening 1
186 | Tinted Glass | increases window reflectivity | Cooling - C | [8 empty] | Yes |  | 1.8878 | 0.79996 | 2.3599 | 1.9416 | Yes | 7785.44 | 4.0892 | GPC EnerSim model | 802 sq ft | Lodging | Amusement, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 3521 | Per square Foot priced from GILA 36"W x 180"L Mirrored Window Film http://www.lowes.com/pd_88148-74130-PRS361_0__?productId=1103235&Ntt=solar+window+film&pl=1&currentURL=%2Fpl__0__s%3FNtt%3Dsolar%2Bwindow%2Bfilm&facetInfo= | 6647.0087 | 10 | DEER EUL_Summary_10-1-08, Reflective Window Films & Sunscreens | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
187 | Vestibule/Revolving Doors |  | Cooling, Heating - C | [8 empty] | No | Difficult to quantify savings - depends on building orientation | bar: Qualitative Screening 1
188 | High Efficiency Water Heating System Design |  | Water Heating | [8 empty] | No | Difficult to quantify savings - depends on baseline equipment and water heating requirements. Individual measures are included in the catalog. (#'s various) | bar: Qualitative Screening 1; Qualitative Screening 3
189 | Low-temperature dishwasher - Conveyer | Commercial grade dishwasher that only requires low temperature water input. | Water Heating | [8 empty] | Yes |  | 999.99 | 0.80995 | 999.99 | 999.99 | Yes | 6774 | 1.6614 | GPC EnerSim model | 1 unit | Lodging | Education, Hospital, Lodging, Office, Restaurant, | 0 | http://www.webstaurantstore.com/wareforce-by-jackson-44l-conveyor-low-temperature-dishwasher-left-to-right/495WF44LLR%20%20208*2303.html | 3950.1799 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
190 | Low-temperature dishwasher - Stationery | Commercial grade dishwasher that only requires low temperature water input. | Water Heating | [8 empty] | Yes |  | 999.99 | 1.2064 | 999.99 | 999.99 | Yes | 3338.17 | 0.37682 | GPC EnerSim model | 1 unit | Lodging | Education, Hospital, Lodging, Office, Restaurant, | 0 | http://www.webstaurantstore.com/wareforce-by-jackson-i-single-rack-low-temperature-straight-dishwasher/495WF1%20%20%20%20%20%20115.html | 3419.9547 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 29610.625 | LO_Medium
191 | Low-water Dishwasher (Energy Star) | Commercial grade dishwasher that only requires low temperature water input. | Water Heating | [8 empty] | Yes |  | 0.8493 | 1.2192 | 0.75953 | 0.86739 | No
192 | Faucet Aerator | 0.5 gpm | Water Heating | [8 empty] | Yes |  | 1.139 | 1.1727 | 1.065 | 1.1578 | Yes | 1851.19 | 0.098245 | GPC EnerSim model | 100 units | Lodging | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 1980 | Price from http://e3living.com/5-gallons-minute-aerator | 2255.1577 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 23688.5 | Fast
193 | Low Flow Showerhead | 1.75 gpm | Water Heating | [8 empty] | Yes |  | 6.602 | 1.1724 | 6.173 | 6.7113 | Yes | 3713.08 | 0.19649 | GPC EnerSim model | 2 units | Lodging | Education, Hospital, Lodging, | 684 | Price from http://www.amazon.com/Showerhead-pressure-compensating-controller-1-75gpm/dp/B002BAZR46/ref=cm_lmf_tit_11 | 4515.7837 | 11 | DEER EUL_Summary_10-1-08, copied "aerator" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 47377 | LO_Fast
194 | Heat Pump Water Heater | commercial HPWH | Water Heating | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 9.5867 | 0.82382 | 11.6368 | 9.9477 | Yes | 39757.76 | 2.7639 | GPC EnerSim model | 1 unit | Lodging | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 2034 | AO Smith Factory Representative with book price for model number AWH115 | 19499.2482 | 10 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
195 | Storage Water Heater | DHW stoarage measure | Water Heating | [8 empty] | Yes |  | 1.2089 | 0.40165 | 3.0098 | 1.2294 | Yes | 5341.39 | 7.5442 | GPC EnerSim model | 1 unit | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 6173 | A.O. Smith TJV-250A Commercial Storage Tank, Jacketed, 250 Gallon, ASME, Custom Line Insulated Storage Tank http://www.plumbersurplus.com/Prod/A-O-Smith-TJV-250A-Commercial-Storage-Tank-Jacketed-250-Gallon-ASME-Custom-Line-Insulated-Storage-Tank/200384/Cat/1667 | 7462.9757 | 11 | DEER EUL_Summary_10-1-08, copied "High Efficiency Gas Water Heater" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -0.22 | 0 | LO_Medium
196 | Temperature set-point reduction |  | Water Heating | [8 empty] | No | Poor customer acceptance, particularly if lower temperature affects customer comfort or processes | bar: Qualitative Screening 5 to Qualitative Screening 6
197 | Timer |  | Water Heating | [8 empty] | No | Difficult to quantify savings - facility operations will dictate timer settings and water requirements | bar: Qualitative Screening 1
198 | Water Heater Cycling |  | Water Heating | [8 empty] | No | Difficult to quantify savings - depends on cycle time, facility water requirements | bar: Qualitative Screening 1
199 | High Efficiency small instantaneous water heaters (30% above the minimum) | point of use WH's | Water Heating | [8 empty] | Yes |  | 9.0073 | 0.81685 | 10.3298 | 9.2045 | Yes | 21517.29 | 4.2553 | GPC EnerSim model | 10 units | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 3670 | Bosch Electric 12 kW 2.0 GPM Powerstream http://www.ecoairandwater.com/store/bosch_rp12pt.html assume 5 lavs per restroom; two restrooms per floor; ten floor 100 total | 33612.2135 | 20 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -4.76 | 153910 | LO_Medium
200 | Heat Recovery from Ref. or A/C |  | Water Heating | [8 empty] | No | Difficult to quantify savings - depends on size and operation of other systems (refrig, A/C) at the facility | bar: Qualitative Screening 1
201 | Heat Trap | U-bend in HW supply to reduce cycling | Water Heating | [8 empty] | Yes |  | 73.5566 | 0.82818 | 88.8176 | 76.2704 | Yes | 17000.24 | 1.9406 | GPC EnerSim model | 1 unit | Hospital | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 124 | http://www.amazon.com/Camco-1013-Dielectric-Heat-Traps/dp/B0006JLVEE | 9121.0151 | 11 | DEER EUL_Summary_10-1-08, copied "High Efficiency Gas Water Heater" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
202 | Solar Water Heater | solar water heater sized for partial or full capacity | Water Heating | [8 empty] | Yes |  | 0.83797 | 0.84463 | 0.99212 | 0.86547 | No
203 | Insulating Blanket (R=11) | Insulation blanket for hot water heater tank. | Water Heating | [8 empty] | Yes |  | 3.4021 | 1.1755 | 2.8941 | 3.5259 | Yes | 420.49 | 0.051088 | GPC EnerSim model | 1 unit | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 50 | http://fierychill.com/components/water-heater-parts/water-heater-insulation-blankets/water-heater-insulation-blanket-r11-3-in-x-48-in-x-75-in-rheem-sp57-11c | 236.8765 | 13 | DEER EUL_Summary_10-1-08, copied "Pipe Insulation - Electric Water Heater" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -2.64 | 0 | LO_Medium
204 | Insulating Blanket (R=6.7) | Insulation blanket for hot water heater tank. | Water Heating | [8 empty] | Yes |  | 4.0292 | 1.1695 | 3.4452 | 4.1757 | Yes | 328.01 | 0.039817 | GPC EnerSim model | 1 unit | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 29 | http://fierychill.com/components/water-heater-parts/water-heater-insulation-blankets/water-heater-insulation-blanket-r6-7-2-in-x-48-in-x75-in-rheem-sp57-67 | 184.1404 | 13 | DEER EUL_Summary_10-1-08, copied "Pipe Insulation - Electric Water Heater" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -2.11 | 0 | LO_Medium
205 | Pipe Insulation | R-2.4 | Water Heating | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 1.3486 | 1.0353 | 1.3026 | 1.3978 | Yes | 5745.79 | 0.64953 | GPC EnerSim model | 622 ft of pipe | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 2662 | http://www.homedepot.com/Plumbing-Pipe-Insulation/h_d1/N-buy9Z5yc1v/R-100111613/h_d2/ProductDisplay?langId=-1&storeId=10051&catalogId=10053 | 3590.0157 | 13 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | Medium
206 | Conversion from dry cleaning facility to professional wet cleaning | reduces energy usage of facility and reduces contaminants to the air | Water Heating | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 4
207 | High efficiency plastic injection molders | utilized VSDs and other efficiency techniques | Misc, Other Elec - I | [8 empty] | No | included in revised industrial measure list - "Plastics Mfr: Injection Molding Improvements"
208 | Pulse cooling for injection molders | replaces existing chilled water system to cool the plastic mold | Misc, Other Elec - I | [8 empty] | No | included in revised industrial measure list - "Plastics Mfr: Injection Molding Improvements"
209 | Wastewater treatment facility retrocommissioning | Includes aerator replacement, control improvements, increased blower efficiency, increased pumping efficiency | Misc, Other Elec - I | [8 empty] | No | Difficult to quantify savings - depends on current condition of facility | bar: Qualitative Screening 1
210 | Thermal oxidizer upgrades | replacement with more efficient unit, heat recovery | Misc, Other Elec - I | [8 empty] | No | Difficult to quantify savings - depends on current condition of equipment | bar: Qualitative Screening 1
211 | Pinch Technology |  | Misc, Other Elec - I | [8 empty] | No | Difficult to quantify savings - depends on baseline set-up and available adjustments | bar: Qualitative Screening 1
212 | Convection-Microwave Dryer |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1
213 | Electric Transit & Freight |  | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific | bar: Qualitative Screening 1; Qualitative Screening 5
214 | Electrofinishing |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
215 | Electroforming |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
216 | Electrogalvanization | may be used for coating sheets or strips of a variety of metals. Preferred to hot dip methods | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
217 | Electron Beam Heating/Drying | baseline is conventional web curing process | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
218 | Electroslag Processing | used to produce high purity, structurally homogeneous metal shapes with smooth surfaces | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
219 | Fluidized Bed Heating |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
220 | Freeze Concentration |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | included in revised industrial measure list - "Food Mfr: Optimization of Operating Parameters"
221 | High Efficiency Heating System Design |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. (#285) | bar: Qualitative Screening 1; Qualitative Screening 3
222 | Induction Heating/Melting | for industrial metalworking | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
223 | Infrared Drying |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
224 | Infrared Curing & Drying |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
225 | Infrared Heating/Melting |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
226 | Ladle Refining | used to desulfurize steels, remove other impurities and hold the molten steel for casting operations. Higher tap temperatures are normally required from steel making furnaces due to heat losses during refining with conventional ladles | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
227 | Laser Processing |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
228 | Microwave Heating/Drying |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
229 | Ozonation |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | included in revised industrial measure list - "Plant Energy Mgmt, Effluent Treatment System, Bldg Improvements"
230 | Plasma Fired Cupola |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
231 | Plasma Processing |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
232 | Radio Frequency Drying |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
233 | Radio Frequency Heating |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
234 | Ultraviolet Curing |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
235 | Vacuum Distillation |  | Other (electrolysis, cogen, steam, space heat, and space cooling) | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
236 | Vacuum Resistance Heating |  | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
237 | E-cube | A device with similar heat transfer characteristics as food, allowing the refrigerator to monitor the more stable food temperature rather than air temperature, resulting in less frequent cycling of the compressor | Refrigeration | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 4
238 | Evaporator Fan ECMotor Controller on Walk-ins | Install a motor controller in a grocery store's walk-in cooler or freezer to reduce the speed of (or turn off) the evaporator fan motors (ECM) when the compressor is not operating. | Refrigeration | [8 empty] | Yes |  | 2.691 | 1.2711 | 2.117 | 2.7865 | Yes | 3826.05 | 0.462 | GPC EnerSim model |  | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 1111 | https://www.hvacusa.com/store/functional-devices-rib-uncategorized-c-1010759_1010816/efc4045t-p-90164749?zenid=4b96fcf66f8ece5633cfac00091f5ba9 | 2989.711 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
239 | Smart Plug Load Power Strips | Load sensing smart plug strips detect the drop in current that occurs when the control device enters a low-power mode. Applications for smart plug strips include workstations, open office cubicles, and other office equipment. | Office Equipment | [8 empty] | Yes |  | 3.7071 | 0.69635 | 5.3237 | 3.8433 | Yes | 29787.83 | 6.0428 | GPC EnerSim model | 20 units | Office | Amusement, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 1671 | http://www.conservationmart.com/p-1760-belkin-conserve-smart-av-power-strip-f7c007q.aspx | 7788.4873 | 5 | http://articles.cnn.com/2007-10-09/living/rs.rx.electronic_1_preventive-medicine-ipod-battery/2?_s=PM:LIVING, copied dvd player | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -134.79 | 0 | LO_Fast
240 | Network PC Power Management | Network PC Power Management - PC power management software intelligently power manages computers across networks remotely and automatically overnight, on weekends and when not in use. | Office Equipment | [8 empty] | Yes |  | 11.6749 | 0.70499 | 16.5603 | 12.1031 | Yes | 114188.39 | 23.8174 | GPC EnerSim model | 94 units (computers) | Office | Amusement, Data Center, Government, Grocery, Hospital, Lodging, Medical Office, Office, Large Retail, Small Office, Small Retail, | 470 | $5 per computer from www. setpowersoftware.com Assumed 300 W per computer, 30 W per monitor, | 29846.9295 | 5 | http://www.ohio.edu/sustainability/greenpc/ | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -522.43 | 0 | Medium
241 | Exit Sign - Photoluminescent or Tritium | Photoluminescent or Tritium Exit Signs | Interior Lighting - C | [8 empty] | No | Only applicable in areas with sufficient natural light | bar: Qualitative Screening 5
242 | Low-Flow Pre-Rinse Spray Valves - 1.6 GPM (Existing to Code) | 1.6 GPM (Federal Standard) - Existing to code | Water Heating | [8 empty] | No | code requirement | bar: Qualitative Screening 2 to Qualitative Screening 3
243 | Low-Flow Pre-Rinse Spray Valves - 0.6 GPM (Code to high Efficiency) | 0.6 GPM - Code to high efficiency | Water Heating | [8 empty] | Yes |  | 762.0167 | 0.84816 | 832.3797 | 776.8705 | Yes | 70578.92 | 6.5067 | GPC EnerSim model | (25 gal/hour) per energy model, peak load from model is 2820 GPH, assume 20% is kitchen load, and 68% is prerinse (6.4 gpm), Base is 1.6 GPM | Hospital | Education, Grocery, Hospital, Restaurant, Large Retail, | 88 | http://www.bricor.com/bestshowerheads/pre-rinse/ | 67057.4716 | 10 | DEER EUL_Summary_10-1-08, copied "Faucet Aerators" | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 652437.5 | LO_Fast
244 | Ground Source Heat Pump | Code (13.4 EER, 3.1 COP) 10 ton closed loop | Cooling, Heating - C | [8 empty] | Yes |  | 0.23488 | 0.66489 | 0.26646 | 0.23666 | No
245 | Variable Refrigerant Flow Heat Pump | Variable Refrigerant Flow Heat Pump | Cooling, Heating - C | [8 empty] | Yes |  | 0.12543 | 0.66063 | 0.18987 | 0.12937 | No
246 | Motor rewind | >15, <500 HP; Green Motors Program | Miscellaneous - I | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
247 | Green roof - vegetated rooftop | A green roof is a roof of a building that is partially or completely covered with vegetation and a growing medium, planted over a waterproofing membrane. Reduces building summer cooling loads by improving the insulation properties. | Cooling, Heating - C | [8 empty] | Yes |  | 0.039641 | 1.1973 | 0.03311 | 0.041217 | No
248 | Drain Heat Exchanger | Copper wound water piping and pumps to preheat water going into water heater. | Water Heating | [8 empty] | Yes |  | 0.35868 | 1.4449 | 0.24824 | 0.36985 | No
249 | Marathon ecopower MCHP System |  | Miscellaneous - C | [8 empty] | No | generation option - outside the scope of energy efficiency analysis | bar: Qualitative Screening 1; Qualitative Screening 5
250 | eco-Button | retro-fit computer power saving device that reduces PC power usage | Miscellaneous - C | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 4; Qualitative Screening 6
251 | Commercial energy recovery ventilation systems | Limited to hot & humid markets; recovery devices consume energy & are least effective when humidity and temp. are similar; most effective during peak times. Market pioneers face lack of understanding by HVAC vendors, and there have been some reliability issues | Cooling, Heating - C | [8 empty] | Yes |  | 1.9955 | 0.60173 | 3.3163 | 2.0562 | Yes | 19523.56 | 4.7831 | GPC EnerSim model | 1 unit, 2,624 cfm | Small Office | Education, Lodging, Medical Office, Restaurant, Small Office, Small Retail, | 9034 | RSMeans Mechanical Page 383 Heat Wheel Air to Air Energy recovery | 18027.4315 | 14 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
252 | Active chilled beam cooling | Instead of conventional variable air volume systems, chilled beam systems allow for small amounts of outdoor air to be entrained into a larger supply of recirculated air, and passed across a radiant-convective "chilled beam" fixture. Systems are quieter and take up less space; eliminate many initial costs by reducing need for ductwork; cheaper and easier maintenance. Lack of awareness, though it is starting to emerge in North America, though typically it has only been used in Northern Europe. Limited to areas that have relatively low cooling demand | Cooling - C | [8 empty] | Yes |  | 0.35835 | 0.82266 | 0.4356 | 0.36797 | No
253 | Advanced (commercial AC) modulating HVAC compressors | Modulating systems are rare, as most systems only have one speed, but competition and an expanded marketplace are changing that. Compressors use 55-80% of total energy for a roof-top unit | Cooling, Heating - C | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
254 | Automated fault detection & diagnostics for rooftop units | Smart features and devices that would recognize when equipment has failed or is operating below efficient levels. Improved maintenance, serviceability and robustness as well as ability for energy managers to better manage consumption | Cooling, Heating - C | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 4
255 | Liquid desiccant air conditioner | Systems offer large energy savings and improved humidity control in applications where latent loads are high relative to sensible loads, including hot-humid climates and grocery stores where low in-door humidity is ideal. These are common but new technology has emerged making them more efficient. Can be used with renewable energy sources, such as solar thermal; improves humidity levels | Cooling - C | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
256 | Waste Heat Recovery | Work with customers to design customized waste heat recovery systems | Heating - C | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
257 | More efficient Real Time Pricing (RTP) | Using remote metering technology for communicating more detailed price signals (improve on hourly RTP prices) | Miscellaneous - I | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
258 | Interruptible Curtailment Technology | Comprehensive systems to remotely curtail electric load (customized for individual plants) | Miscellaneous - I | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
259 | Efficient Aluminum Melting Technologies | Energy efficient melting & direct delivery of high quality molten aluminum | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
260 | Aluminum Forming Technologies | Hot rolling scrap reduction through edge cracking and surface defects control | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
261 | Chemical Separations Technologies | Advanced membranes technology platform for hydrocarbon separations | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
262 | Chemical Separations Technologies | Ammonia production using pressure swing adsorption | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
263 | Chemical Separations Technologies | Distillation column flooding predictor | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
264 | Chemical Separations Technologies | Heat integrated distillation through use of microchannel technology | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
265 | Chemical Separations Technologies | Low cost chemical feedstocks using an improved & energy efficient natural gas liquids removal process | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
266 | Chemical Separations Technologies | Novel catalytic membrane reactors | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
267 | Chemical Reactions Technologies | Advances in process intensification through multifunctional reactor engineering | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
268 | Chemical Reactions Technologies | Development of highly selective oxidation catalysts by atomic layer deposition | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
269 | Chemical Reactions Technologies | Microchannel reactor system for catalytic hydrogenation | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
270 | Chemical Reactions Technologies | Millisecond oxidation of alkanes | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
271 | Chemical Reactions Technologies | Using ionic liquids in selective hydrocarbon conversion processes | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
272 | High Efficiency Pulping | Highly energy efficient directed green liquor utilization pulping | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
273 | Improved Fiber Recycling | Development of screenable wax coatings & water based pressure sensitive adhesives | Misc, Other Elec - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Other' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
274 | Next Generation Melting Systems | Energy efficient glass melting: submerged combustion melting & rapid conditioning | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
275 | Advanced Melting Technologies | E-SMARRT: energy saving melting and revert reduction technology | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
276 | Innovative Casting Processes | In-situ real time monitoring & control of mold making & filling processes | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
277 | Advanced Process Development | Minimization of blast furnace fuel rate by optimizing burden & gas distributions | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
278 | Advanced Process Development | Thermochemical recuperation for high-temperature furnaces | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
279 | Cokeless Ironmaking | Next generation metallic iron nodule technology in electric furnace steelmaking | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
280 | Cokeless Ironmaking | Paired straight hearth furnace | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
281 | Next Generation Steelmaking | Development of next generation heating system for scale free steel reheating | Thermal - I | [8 empty] | No | Limited applicability - only useful for particular industrial processes, also difficult to quantify because operations are site specific. Simplified measure 'Industrial - Thermal' added to capture potential savings. | bar: Qualitative Screening 1; Qualitative Screening 5
282 | Boiler Control Technology |  | Thermal - C | [8 empty] | No | Difficult to quantify savings | bar: Qualitative Screening 1; Qualitative Screening 5
283 | Duct Testing & Sealing |  | Cooling, Heating - C | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.98853 | 0.65244 | 1.5151 | 1.0232 | No
284 | High Efficiency Water Heater - 50 gal. EF= .94 (base=.86) | Energy Star does not rate water heaters | Water Heating | [8 empty] | Yes* | Program currently in place-"Georgia Power's Commercial Energy Efficiency Program." | 0.32766 | 1.1476 | 0.28553 | 0.33849 | No
285 | Industrial - Thermal | Multiple industrial measures for which savings were difficult to quantify were combined and simply modeled as an assumed overall percent savings. | Thermal -I | [8 empty] | No | included in revised industrial measure list - Process-Thermal measures
286 | Industrial - Other | Multiple industrial measures for which savings were difficult to quantify were combined and simply modeled as an assumed overall percent savings. | Other - I | [8 empty] | No | included in revised industrial measure list - Other, Bldg Improvements, Process improvements
287 | Energy Star Imaging Equipment | saves 15% on office equipment | Office Equipment | [8 empty] | Yes | Combination of ID #'s 28, 30, 31, 33-35 | 0.40409 | 0.69232 | 0.58368 | 0.41951 | No
288 | Cold Plasma Technology for IAQ | Uses cold plasma to produce O3 allowing for lower outside air rates. | Cooling, Heating - C | [8 empty] | No | EPA recommends against using Ozone Generators for contaminant control/ventilation (http://www.epa.gov/iaq/pubs/ozonegen.html). Difficult to quantify savings. | bar: Qualitative Screening 1; Qualitative Screening 7
289 | Transpired Solar Collector | Unglazed solar collectors have been used in the past for preheating ventilation air for a building. These solar collectors typically include a dark absorber panel, positioned to face the sun, and a plenum or air collection space into which the heated air is drawn through perforations or holes in the absorber panel. The movement of air is often aided by fans or some source of suction to draw the air into the plenum and distribute it throughout the building. It was believed that absorbers had to be constructed of high thermal-conductivity materials such as copper or aluminum to avoid overheating in regions away from the holes, which would reduce overall efficiency due to radiative loss of heat. | Miscellaneous - C | [8 empty] | No | outside the scope of energy efficiency analysis
290 | Energy Efficient Laboratory Fume Hood | Helmut Feustel at Berkeley Lab has developed a promising new low-flow method that reduces this energy load in fume hoods, while still protecting workers' health. This new constant air volume system can reduce a laboratory's energy consumption and peak-power requirements for fan and make-up air conditioning energy. Because of this reduced make-up air requirement, air-conditioning equipment can also be downsized, which reduces initial equipment costs and space requirements for the air handler and the ductwork. The new Berkeley Lab fume hood also does not require the expensive control systems used to regulate air flow in VAV fume hoods. | Miscellaneous - C | [8 empty] | Yes |  | 12.0973 | 0.94345 | 12.8224 | 12.5431 | Yes | 2127.7082 | 0.20512 | GPC EnerSim model | 500 CFM | Education | Education, Government, Medical Office, | 128.5557 | RSMeans Online | 1555.173 | 15 | DEER EUL_Summary_10-1-08 copied fan powered mixing boxes | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
291 | Heat Transfer Interface for Thermo-Solar Energy | In one aspect of the Berkeley Lab technology, nanotube forests are attached to the exterior of a heat exchanger to absorb sunlight with high efficiency. In a second aspect, nanotube forests are mounted to the interior of a heat exchanger and functionalized to work in concert with heat transfer fluids. In the case of water as a heat transfer fluid, for example, a superhydrophilic functionalization of the nanotube forests improves the thermal transfer between the heat exchanger wall and the water being heated inside. As a result, sunlight efficiently heats the outside of the heat exchanger that, in turn, heats the water flowing within its interior. The water turns to steam and performs mechanical work via a steam turbine or other machine. Other fluids such as molten metals and salts as well as gases can be utilized in this technology. This invention will be of interest to utility companies investing in power plant improvements as well as farmers or homeowners seeking to generate their own power. The components of the technology could be used to improve heat transfer in industrial, commercial and home heating and cooling systems; internal combustion engines; and in electronic devices, such as notebook computers, that frequently overheat. | Heating - C | [8 empty] | No | http://techportal.eere.energy.gov/technology.do/techID=29 reference lists technology as available however no sources were found for efficiency improvements nor premimum to add technology to existing solar equipment. | bar: Qualitative Screening 1; Qualitative Screening 4
292 | Hedgehog™ Water Contaminant Removal System | In arsenic decontamination testing, small water systems (~100 connections or less) with ambient arsenic (As) levels of 11-25 ppb could achieve low cost compliance with the new US arsenic limit of 10 ppb by using this in-tank filtration system. Estimates indicate results would be similar in other types of contaminants. The smaller scale, greater efficiency, and reduced cost of this filtration system make it a viable option of small tank owners and communities. The annual cost for the Hedgehog™ is approximately 1/3 of the GIM option which supports the notion that the smaller the system, the more appropriate the in-tank treatment system becomes. | Miscellaneous - C | [8 empty] | No | Not available commercially. We could not find a distributer for an avg cost of installation. Appears to be more focused on addressing water quality issues and wider applicability of arsenic decontamination than producing energy savings; no technical specifications were found to calculate energy savings. | bar: Qualitative Screening 1
293 | Synthesis of High Efficiency Thermoelectric Materials | Bulk thermoelectric materials are heated above their melting temperature. They are then cooled at a rate of at least 100,000K/s, and up to in excess of 1,000,000K/s, by melt-spinning. The resulting nanoribbons of material are then hot-pressed or subjected to spark-plasma sintering for a matter of minutes. The end result is a thermoelectric material with ZT about 20% to 50% higher than the bulk value | Miscellaneous - C | [8 empty] | No | Not currently available; and appears to only be applicable to specific processing operations | bar: Qualitative Screening 1; Qualitative Screening 4 to Qualitative Screening 5
294 | Decision Support for Operations and Maintenance (DSOM) | DSOM integrates plant operations, energy management, and maintenance processes. It provides operators and engineers with information such as equipment health; real-time and long term trending of critical operational parameters; and, operational requirements for cost-effective operating decisions. | Miscellaneous - C | [8 empty] | No | Difficult to quantify cost and energy savings. Savings may overlap with savings achieved through retro-commissioning and re-commissioning measures, which provide similar O&M manuals/guidelines | bar: Qualitative Screening 1
295 | Facility Energy Decision System (FEDS™) Software | FEDS Software makes assessments and analyzes energy efficiency in single or multiple buildings. Users can quickly compare energy savings potential across different sites through multiple FEDS runs. It provides an easy-to-use tool for identifying minimum life cycle cost retrofits, determining payback, and enabling users to prioritize options. | Miscellaneous - C | [8 empty] | No | Limited applicability. Zero cost but only available to state-owned facilities. Program also only appears to identify opportunities but not produce energy savings on its own. Savings identified likely includes other measures in Tech Catalog | bar: Qualitative Screening 1; Qualitative Screening 5
296 | Rooftop Diagnostician | The Rooftop Diagnostician attaches directly onto the HVAC unit and provides real-time web-based performance information. It allows you to remotely monitor the functionality of a rooftop unit in order to easily and cost-effectively evaluate performance. Developed at PNNL, this tool allows you to determine the cause of a malfunction in a rooftop unit or to monitor performance in order to optimize regularly scheduled maintenance. | Cooling, Heating - C | [8 empty] | No | No specific cost nor specific energy savings data available. Provides data on HVAC performance but energy savings are dependent on system and user response to information | bar: Qualitative Screening 1
297 | Rapid Cooling Using Ice Slurries for Industrial and Medical Applications | HVAC is the largest energy consumer in commercial buildings in the U.S., accounting for over a third of total energy consumption. One solution is to use ice slurry coolants in HVAC systems, which can increase cooling efficiency and substantially lower operational and equipment costs over chilled water systems. Argonne researchers have been conducting key research on using ice slurry coolants for HVAC applications. However, a major bottleneck was the ability to produce slurry with ice loadings approaching 50% by weight, store it, and then distribute it in a piping network without plugging the pipes. Argonne researchers solved that problem by engineering a proprietary ice slurry containing ice particles that are globular and smooth. As a result, the ice slurry can be stored in a tank without agglomeration and can be pumped through pipes at very high ice particle loading without plugging. Ice slurry technology is not limited to HVAC applications: Argonne researchers, working with University of Chicago (UC) doctors, have developed and patented a special ice slurry that can be injected intravenously, intra-arterially, over the external surfaces of organs by using laparoscopy, or even via endotracheal tube. The ice slurry selectively cools organs to prevent or limit ischemic damage after a stroke or heart attack. Researchers have successfully completed medical exploratory slurry tests on animals that simulated such conditions as in-hospital kidney laparoscopic procedures. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1
298 | Electrical Cable Testing by Pulse-Arrested Spark Discharge (PASD) | The PASD technique uses a high-voltage, low-energy, short pulse to induce an electrical spark breakdown at the site of an insulation defect. The pulse energy is insufficient to damage insulation or the conductors within wiring systems. PASD has been demonstrated to be effective in several challenging environments and has consistently detected wiring system defects which cannot be seen through visual inspection. | Miscellaneous - C | [8 empty] | No | Does not appear to be an energy savings measure, but is for electrical wiring insulation. No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1
299 | Novel Structured LED and OLED Devices | This technology uses structured approaches to LED and OLED architecture as an alternative to conventional, unstructured multi-layer films for LED and OLED devices. In LEDs, the structured features reduce lattice strain, thus decreasing defects and improving efficiency. Prior to the Berkeley Lab technology, developers of short wavelength LED devices had not found a satisfactory solution to the problem of high defect concentration. This technology uses micro and nanoscale heteroepitaxy to achieve a semiconductor island structure of high crystalline quality for covering the substrate. Similarly, light extraction, particularly for OLEDs, remains an obstacle to achieving high performance devices. This invention offers a solution based on intrinsic device architecture rather than complicated external optical elements. | Exterior Lighting, Interior Lighting - C | [8 empty] | No | Difficult to quantify cost and energy savings.No specific cost nor specific energy savings data available. LED replacments for incandescent bulbs are currently in the Tech Catalog ID#'s 3,4,5,11, and 110. | bar: Qualitative Screening 1; Qualitative Screening 4
300 | High Performance OLEDs with Air-stable Nanostructured Electrodes | This technology represents a significant improvement over existing technology. Currently, the interface between an OLED device’s cathode and organic layer is a resistant barrier that inhibits the efficient flow of electrons. This barrier can also create heating that damages the OLED. Additionally, low work function metals used to reduce operating voltage and improve device yield are physically and chemically unstable and difficult to fabricate into a thin layer. The Air-stable Nanostructured Electrodes promise to significantly reduce the drive voltage necessary to induce light emission inside organic materials and will thereby increase the energy conversion efficiency of the OLEDs. The ordered arrangements of nanostructures or nanomaterials to enhance charge injection efficiently overcome the large energy barrier at the cathode-organic layer interface. Charge balance between holes and electrons is improved, a steeper rise in current as a function of voltage is realized, and electrical-optical conversion efficiency is increased. Using less reactive materials makes the cathode more resistant to degradation than conventional metal electrodes. This feature increases OLED device lifetime, simplifies packaging requirements and makes it amenable to scale-up manufacturing processes. | Exterior Lighting, Interior Lighting - C | [8 empty] | No | No specific cost nor specific energy savings data available. Product still appears to be in development phase and unclear the level of efficiency gains over current LED technologies that are included in Catalog | bar: Qualitative Screening 1; Qualitative Screening 4
301 | Aerosol Remote Sealing System | Berkeley National Laboratory's aerosol compound seals holes in enclosed systems and is effective even after bends and junctions. A unique, in situ aerosol sealing apparatus, also designed and built at Berkeley National Laboratory, delivers the new sealing aerosol. This multifunctional field apparatus, designed to be portable and easy to use, is powered by two, household circuits (15A/110V) and does not require the use of desiccants. In addition to performing the sealing process, Berkeley National Laboratory's compact field apparatus also measures leakage of the system before and after sealing, eliminating the need to invest in and field additional equipment. A description of the clog-free atomizing and spray drying nozzle specially designed for use with this technology is referenced below. | Cooling, Heating - C | [8 empty] | No | No commercial product found. | bar: Qualitative Screening 1
302 | Clog-free Atomizing and Spray Drying Nozzle | The Berkeley Lab nozzle can be fed with heated gas for spray drying or unheated gas for just atomization and can be constructed from standard tube fittings. Hand-tightened installation of the liquid tube makes servicing easy. In addition, the design has been shown to reduce energy use by 80 percent for some applications. For more information on this technology see: http://epb1.lbl.gov/aerosol/Atomizer.html | Miscellaneous - C | [8 empty] | No | No commercial product found and specific to specific process operation. Savings very dependent on usage characteristics which may vary widely between facilities. | bar: Qualitative Screening 1; Qualitative Screening 5
303 | Novel Electrochromic Device Controlled by Sunlight | Direct exposure to natural sunlight transforms exposed areas of the electrode from transparent to gray. Nonuniform illumination produces patterned optical states that can be stored or erased using optical read/write capability. Berkeley Lab's new electrode is ideal for 'smart windows' that can use either an external power source or incident sunlight to modify light transmission. Other potential applications include photochromic ophthalmic lenses; tunable neutral density filters; photosensitive mirrors, displays, light detectors, optical switches, light-intensity meters, near-UV radiation detectors, and low-cost optical computer memories. Use of inexpensive components combined with simple construction (only 3 layers compared to 5 in competing electrodes) widens the applicability of such devices, and significantly reduces the cost, compared with related technologies. | Miscellaneous - C | [8 empty] | No | No commercial product found - appears to still be a technology under development that has potential for applications in Smart Windows, but has not been produced to date. | bar: Qualitative Screening 1; Qualitative Screening 4
304 | First Diode for Thermal Management of Micro and Macro Devices | The Berkeley Lab nanoscale solid state device is to thermal systems what the diode is to electronics. Controlling the direction of heat flow could lead to radical improvements in thermal management across a range of products. For example, the Berkeley Lab thermal diode might prevent overheating in microelectronic devices, currently a barrier to significant size reductions. Since the technology can be designed to handle high macroscopic thermal current densities, it may also lead to more efficient refrigerators, solar cells, and buildings. The new thermal diode could also result in computing systems that use phonons instead of, or in addition to, electrons for manipulating and transporting information bits. | Miscellaneous - C | [8 empty] | No | Currently in development and unclear what specific product/application technology would be applied to. | bar: Qualitative Screening 1; Qualitative Screening 4
305 | Low Cost, Stable Switchable Mirrors: Lithium Ion Mirrors with Improved Stability | Applications for the new Berkeley Lab electrochromic materials described below include architectural glass, sunroofs, rear view mirrors, aerospace insolation controls, optical switching elements, and thin film displays. Thomas Richardson of Berkeley Lab has developed a switchable mirror system based on lithium ion insertion that is inherently more stable than systems based on metal hydrides. Hydride systems suffer from poor life cycle due to the highly reactive nature of the active metal film which is easily and irreversibly oxidized by air or water. Because the Berkeley Lab device is sealed and the component electrode materials are stable with respect to the non-aqueous electrolyte, irreversible degradation of the mirror film is avoided. The devices can be made using less expensive fabrication methods and do not require the protective palladium layer needed in hydride mirrors. A typical device consists of a thin reflective film of active material such as antimony applied to a glass substrate. The electrolyte may be a solid, liquid, or polymer. A counter electrode supplies positive lithium ions and may be transparent, opaque, reflecting, or electrochromic, depending on the application. When a potential is applied, electrons flow into the active metallic layer. At the same time, lithium ions are taken up by the metal to form a new transparent compound. The transition may be stopped or reversed at any point to achieve a desired level of transparency or reflectivity. Infrared radiation is modulated even more effectively than visible light, raising the prospect of improved energy efficiency. | Miscellaneous - C | [8 empty] | No | Currently in development stage - No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
306 | Transition Metal Switchable Mirrors | A window using this technology can be programmed to respond to local sunlight and weather conditions, optimizing the amount of daylight entering a building, while controlling the gain or loss of infrared radiation or heat. When the sun is bright, TMSMs switch to a highly reflective state; in lower-light, the window can be switched to a partially-reflective state. This new technology could save a fourth or more of the energy lost through windows, currently about $33 billion a year.The use of transition-metals instead of rare earth metals could significantly lower the cost of these windows. The transition metal mirrors are less expensive and easier to manufacture, as they use fewer and thinner coatings. Berkeley Lab's technology performs better than absorbing electrochromic (AE) windows in a number of ways. Their greater dynamic range, both in transmission — from 50% to 0.5% or lower — and in reflection — from 75% to 10% — gives them considerable advantages over AEs in providing user comfort and energy savings. While current electrochromic window materials can darken a window, they have little effect on infrared radiation, which accounts for almost half of incident energy. TMSMs reflect both infrared and visible light, providing much better energy conservation. Applications include windows for offices, homes, autos and airplanes; spacecraft components; and optical switching elements. The technology can also be used in helmets for pilots and motorcyclists. TMSMs offer increased safety by controlling glare. They also reduce a vehicle's heat intake, enabling reductions in the size and weight of air conditioning units, which in turn reduces fuel use. The Berkeley Lab films are expected to be more resistant to oxidation than the rare-earth based films. This characteristic would reduce the need for a full area palladium (Pd) oxidation-resistant coating which has the disadvantage of reducing transparency. "Low-e" windows, the first generation of energy-efficient windows, were developed by Berkeley Lab and its commercial partners during the 1980s. | Miscellaneous - C | [8 empty] | No | Currently in development stage - No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
307 | TRAMS: A New Tracer Gas Airflow Measurement System | Duo Wang, a researcher of the Environmental Energy Technologies Division (EETD) at Lawrence Berkeley National Laboratory (Berkeley Lab) has invented a new tracer-gas measurement method that overcomes these limitations. TRAMS uses carbon dioxide (CO2) as its tracer gas for a number of reasons: CO2 is inexpensive, non toxic, and widely available in cylinders, and CO2 analyzers are much less expensive than the analyzers used for conventional tracer gases, such as sulfur hexafluoride. To ensure that injected CO2 mixes effectively in the airstream, TRAMS uses “whip” injectors (Figure 1). These injectors are very small, flexible tubes that are easily installed in duct systems and emit CO2 at high velocity, which causes them to whip around rapidly in the airstream, dispersing the tracer gas. Easily insertable fans (Figure 2) with fold-up blades and externally mounted motors help mix the tracer gas with the airstream. The soaker-hose sampling system for the CO2 analyzer allows a user to easily collect samples. | Miscellaneous - C | [8 empty] | No | Currently in development stage - No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
308 | Gas Filled Panels | Robert Cheng at Lawrence Berkeley Laboratory originally developed a weak swirl burner as a better way to stabilize flame for scientific study. As with many purely scientific investigations, the resulting device is a better performer than those commercially available. The new burner produces almost no NOx, the chemical responsible for ozone in the lower atmosphere. The shape and temperature of the flame are responsible for the improvement, but the actual result will be device dependent. The simplicity of the new design eliminates device scaling and tolerance problems thereby aiding manufacturability. The design could replace most medium and small scale burners with flame temperature requirements below 2,600deg.F. Market Driver: NOx is responsible for the dirty brown air over most U.S. cities. More than 100 U.S. cities have unsafe ozone levels that exceed federal health standards. Many cities are considering limiting installation of new conventional gas burners. Government energy-saving incentives and pollution control regulations like those for efficient lighting and auto emissions should cause the market to grow at a rapid pace. | Cooling, Heating - C | [8 empty] | No | Difficult to quantify cost and energy savings. No cost for product found. Primary application appears to be in appliances, where savings would be accounted for in appliance efficiency level. | bar: Qualitative Screening 1; Qualitative Screening 5
309 | Tunable Thermal Link | lex Zettl, Arun Majumdar and their teams at Lawrence Berkeley National Laboratory have developed telescoped multiwall nanotubes that can be variably controlled, providing the first step toward a fully functional thermal transistor, and removing the main obstacle for heat management and for the processing of phonons as information carriers. Multiwall nanotubes have a very high intrinsic thermal conductance. If a nanotube is geometrically damaged, its thermal conductance is decreased. The thermal conductance of an individual multiwall carbon nanotube can be controllably and reversibly adjusted by sliding the outer shells in and out of the inner core. The conductance drops dramatically (by 85 percent of the original value) after the length of the tube is extended as the nanotube is telescoped out and the core tubes slide from the remaining “housing.” An exponential increase in the thermal resistance occurs with telescoping distance. The invention would typically include numbers of multiwall nanotubes connected to a heat source and a heat drain and various means of tuning the overall thermal conductance. Although at present controlled by mechanical actuation, it could also be controlled by a thermal gate utilizing thermal expansion of materials. Tunable nanoscale thermal links have immediate implications for nano- to macroscale thermal management, biosystems, and phononic information processing. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
310 | Thermoelectric Ambient Energy Harvester | The Thermoelectric Ambient Energy Harvester uses an assembly of ultra-thin thermocouples in a unique configuration that can exploit small (>2°C) temperature differences occurring naturally in the environment of the application (i.e. ground to air, water to air, or skin to air interfaces). The TEG is constructed from reliable and stable components that offer maintenance-free, continuous power for the lifetime of the application. The individual thermocouples, which are typically no more than 1 cm high by 1.5 cm wide and only a few micrometers thick, are deposited in a linked “chain” onto a thin, flexible plastic substrate (similar to camera film), using sputtered thin-film deposition techniques developed by PNNL. This plastic substrate is coiled around a spool enabling up to several thousand thermocouples to be assembled into a cylindrical TEG 1 to 2 cm in diameter. Depending on the magnitude of the temperature range they experience, their electrical output can be designed over a range from a few microwatts to 100’s of milliwatts and more. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
311 | Techniques for Growth of Lattice-Matched Semiconductor Layers For the fabrication of multi-junction solar cells, light emitting diodes, and high speed transistors | Our existing portfolio of lattice matching technologies aims to find solutions by matching the lattice structures of the various materials so that one may be grown on another to provide the desired device properties and performance. In particular, this portfolio allows for the use of low-cost and scalable processing methods and substrates for growing III-V materials and the reuse of those substrates to dramatically reduce production costs. In addition, the portfolio provides various schemes for growing certain types of III-V material combinations to provide desired bandgap energies capable of absorbing a certain range of energy for PV applications, or for emitting certain wavelengths of light in solid-state lighting applications, or for fabricating high speed or high power transistor devices. As one example, the technologies can be used to grow lattice-matched InGaN alloys for fabrication of a green LED. InGaN alloys are of great interest for the manufacture of light emitting diodes and lasers for use in solid-state lighting applications. However, there is presently a difficulty in creating devices that emit light efficiently at wavelengths between 500 nm and 600 nm, known as the “green gap.” One possible cause of this is that material quality in this region is degraded due to a tendency toward phase separation of the InGaN. The present invention provides a solution by growing lattice-matched InGaN alloys in which phase separation can be suppressed. Another application of the invention is the fabrication of high electron mobility III-V heterostructures suitable for high-speed transistors that can leverage existing semiconductor chip manufacturing infrastructure and processes. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
312 | Microbially Mediated Method for Making Semiconductor Nanoparticles | Nanoparticles with metal non-oxide compositions, also known as semiconductor or quantum dot nanoparticles, are increasingly used in a wide range of electronics, including LED displays, solar cells, and medical imaging. Yet the energy requirements of current production methods are too costly for commercial applications. The invention facilitates economical output of tailored nanoparticles via a scalable production scheme. In addition, the invention has the capability of defining the size, shape, composition, and/or crystalline structure of the nanoparticles. The location or width of the photoluminescent peak can also be controlled. Through the process of bacterial metabolism, the desired non-oxide compound is produced and may be collected as nanometer-sized particles. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
313 | Security Risk Assessment Methodologies (RAM) for Critical Infrastructures | Types of RAMs: •BioRAM for Biological Facilities •RAM-C™ for Communities •RAM-CF™ for Chemical Facilities •RAM-CI for Critical Infrastructures •RAM-DSM for Dams •RAM-E for Energy Infrastructures •RAM-PSM for Prisons •RAM-TSM for Transmissions •RAM-W™ for Water Utilities | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. Does not appear to be a technology that targets energy savings | bar: Qualitative Screening 1
314 | Regenerator for Magnetic Refrigerants | These materials may thus have improved properties for magnetic refrigeration. As part of an effort to research and develop magnetic refrigerants, ISU and Ames Laboratory researchers have developed a special rare-earth aluminum alloy that can be used at low temperatures (sub liquid hydrogen) for Active Magnetic Regenerator (AMR) magnetic refrigerators. This system allows for cyclic heat disssipation and heat absorption in the course of the alternative magnetization and demagnetization as the materials are moved in and out of the magnetic field. This invention can utilize a dual stage active magnetic regenerator for cooling from 77 K (liquid nitrogen boiling point) to 20 K (liquefaction temperature of hydrogen). | Cooling, Heating - C | [8 empty] | No | Currently in development stage - No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
315 | Production of Giant magnetocaloric Substances Using Commercially Available Raw Materials | This new method allows for cost effective production of Gd5(SixGe1-x)4 samples of 1 kilogram or more, which have improved magnetocaloric porperties over material produced by othe methods. (The magnetocaloric effect is approximately 25% better than the first reported values (Physical Review Letters, June 1997) for the Gd5(Si2Ge2) which was prepared in 10-20g quantities by arc melting using high purity Ames Laboratory Gd metal). | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
316 | Method for Creating Photonic Band Gap Materials | Microstructures that produce photonic band gaps have been produced using a layer-by-layer fabrication method, as well as by silicon processing and wafer-bonding techniques. However, these methods require specialized equipment or clean room facilities, and can also result in microstructures that may be misaligned or subject to delamination. To overcome these issues, ISU and Ames Laboratory researchers have developed a method for producing photonic band gap materials that uses microtransfer molding. The microtransfer molding technique is a method whereby a layer is accurately deposited and then transferred onto the lattice structure of the photonic crystal. | Miscellaneous - C | [8 empty] | No | Technology that appears to still be in development stage without a commercial product/application currently. No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
317 | Fabrication of Emissible Metallic Layer-by-Layer Photonic Crystals Using Microtransfer Molding with Electro-Deposition | The efficiency of conventional incandescent light bulbs is very low, with more energy producing heat than light. Newer lighting technologies, such as compact fluorescent bulbs or light-emitting diodes (LEDs) have gained increasing interest with energy security becoming an important national issue. However, anti-flickering and light quality issues still exist with LEDs and compact fluorescent bulbs. In addition, fabrication costs and the requirement for more complicated circuitry make these alternatives less attractive economically. To overcome these drawbacks, ISU and Ames Laboratory researchers have developed a method for increasing the efficiency of traditional incandescent light bulbs that uses a stand-alone filter to recycle photons from emitted infrared light. This approach enables recovered infrared red to be used to maintain filament temperatures required for illumination and decreases the energy needed for comfortable light quality. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. | bar: Qualitative Screening 1; Qualitative Screening 4
318 | Autonomous Combustion-Powered Hopping Robot | Two versions of the robots exist. One being about the size of a grapefruit and capable of approximately 4,000 hops on a single tank of fuel (less than an ounce) of about 3 feet high and 6 feet from the starting point of the jump. The other is about the size of a shoe box and able to overcome as many as 30 obstacles that are over 20 feet high with about 100 hops per tank of fuel. The four-wheeled version of the robot overcomes traditional barriers associated with long-range missions and terrain including management of shock forces, hop height, and efficiency. Furthermore, the robots are equipped with compasses or GPS that allows them to orient themselves once landed. | Miscellaneous - C | [8 empty] | No | gas related measure | bar: Qualitative Screening 1
319 | Process for Fabrication of Efficient Solar Cells | Polymer-based photovoltaic devices have received intense interest in recent years because of their potential to provide low-cost solar energy conversion, flexibility, manufacturability, and are light weight. However, the efficiency of organic solar cells is about 4-6%, and increasing this efficiency is critical for developing practical applications and commercially viable devices. One approach to increasing efficiency is to increase the light absorption on the organic film without increasing the thickness of the photoactive layer, and various light management techniques have been tried for enhancing optical absorption, such as collection mirrors, patterned substrates and microprism substrates. However, these approaches require extra processing steps or technically challenging coating technologies. To overcome these limitations, Ames Laboratory researchers have developed a process for conformal coating of polymer photovoltaic layers on microtextured substrates for increased light trapping. The light management architecture of these solar cells enables a high degree of light absorption in even very thin photoactive films and leads to improved power conversion efficiency. | Miscellaneous - C | [8 empty] | No | Currently in development. | bar: Qualitative Screening 1; Qualitative Screening 4
320 | Advanced Analysis Software Key to New, Energy-Efficient Technologies Leveraging Scientific and Engineering Know-How to Advance Sources of Renewable Energy | Hydropower To support DOE’s goal of increasing generation from existing hydropower facilities, Argonne is leading the development of an integrated modeling and simulation toolkit dealing with water forecasting, reservoir and power supply modeling, stream flow routing, and hydropower unit performance metrics. The toolkit will enable the optimization of hydropower operations and environmental performance and improve the ability of plant operators to manage the risk of hydrological uncertainty. Argonne is leading a multi-laboratory project team that includes Oak Ridge, Pacific Northwest, and Sandia National Laboratories. Wind Power Forecasting and System Integration Key challenges in meeting DOE’s target of 20% wind power by 2030 are the need for enhanced wind forecasting and better integration of wind plants into power system operation. To meet these challenges, Argonne is developing new unit commitment models that account for wind uncertainty, as well as leading an international team developing improved methodologies for short-term wind forecasting. Building Efficiency Buildings use more energy than any other sector of the U.S. economy, consuming over 70% of electricity and over 50% of natural gas. Argonne’s research team is working to deliver important new technologies to the market that will help reduce energy use and make new and existing buildings more energy efficient. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. Software tool appears to still be in development phase and is not a measure | bar: Qualitative Screening 1
321 | PCMs (Phase Change Materials) -Thermal Storage |  | Cooling, Heating - C | [8 empty] | No | Currently in Technology Catalog NonRes ID# 89 - Full Thermal Energy Storage from GDS' 07/26/11 email. Added 08/03/11 | bar: Qualitative Screening 1
322 | Thin-Film Lithium-Based Electrochromic Devices | Electrochromic cells change their light transmission characteristics based on the direction of an applied electric field. In short, they are comprised of an electrolyte sandwiched between two electrodes (a cathode and an anode), where each electrode will darken or bleach based on the flow of ions (and electrons) in or out of the electrode. For lithium-based electrochromic cells, the electrolyte contains mobile lithium which enables lithium ion transfer between the electrodes. The present technology provides both a cell structure and method for fabricating that structure yielding improved performance, cost and stability. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. This measure describes a technology that has potential for application to commercial products, such as windows, but does not appear to be fully developed into a specific product. | bar: Qualitative Screening 1; Qualitative Screening 4
323 | Light Emitting Diodes Based on Lattice-Mismatched GaInP AlloysIA new approach to fabricating green LEDs | Light emitting diodes are the promise of the future because, unlike tungsten bulbs or compact florescent bulbs, they deliver most of their energy as light, rather than heat. The U.S. Department of Energy expects to phase out tungsten bulbs by 2014, and compact fluorescents by 2020, leaving LEDs with virtually the entire market. Current white light generation techniques rely on color mixing from red, blue and green light. While reasonable red and blue LEDs are available for this scheme, availability of a good green LED poses a significant technological challenge. There currently exists a gap in the wavelength spectral window from roughly 530 nm to 570 nm, known as the “green gap,” where realization of efficient green LEDs is proving to be very difficult. | Exterior Lighting, Interior Lighting - C | [8 empty] | No | No specific cost nor specific energy savings data available. This technology applies to manufacturing techniques for LED bulbs, but does not include a commercially available measure, nor describe a measure that produces additional energy savings beyond the other LED lighting measures already included in the catalog. | bar: Qualitative Screening 1; Qualitative Screening 4
324 | Alternating Current Photovoltaic Building Block ACE Plug-N-Play | This technology provides a fully integrated and self-containing alternating current (AC) photovoltaic (PV) Building Block device and method that allows photovoltaic applications to become true plug and play devices. The Building Block combines, contains, and integrates almost all of the electrical and mechanical elements of a PV system while eliminating the traditional DC voltage concerns of todays PV systems. | Miscellaneous - C | [8 empty] | No | No specific cost nor specific energy savings data available. Appears to be in prototype stage and this technology does not appear to provide additional or unique energy savings beyond the solar PV measures already being considered in the catalog. | bar: Qualitative Screening 1; Qualitative Screening 4
325 | Efficient Polymer Solar Cells | Ames Laboratory researchers have developed a process for producing more efficient polymer solar cells by increasing light absorption through a thin and uniform light-absorbing layer deposited on a textured substrate. | Miscellaneous - C | [8 empty] | No | Difficult to quantify cost and energy savings.No specific cost nor specific energy savings data available. Current polymer solar cells are approximately one third efficient than the current efficiency of hard materials (http://en.wikipedia.org/wiki/Polymer_solar_cell) | bar: Qualitative Screening 1; Qualitative Screening 4
326 | ECM Case Motors | Retrofit of "shaded pole" motors with ECM motors. Refrigerated case motors only (smaller). | Refrigeration | [8 empty] | Yes |  | 1.0147 | 0.84859 | 1.1957 | 1.0507 | Yes | 19477.97 | 2.352 | GPC EnerSim model | 15 motors | Grocery | Amusement, Education, Grocery, Hospital, Lodging, Medical Office, Large Retail, Small Retail, | 15000 | http://www.amazon.com/35100-Arktic-59-Electronically-Commutated/dp/B004WSQWQM | 15220.2719 | 16 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | 0 | 0 | LO_Medium
327 | T8 lamp (any length) electronic ballast | Magnetic ballast to Electronic retrofit | Interior Lighting - C | [8 empty] | Yes |  | 2.3207 | 0.81182 | 2.8587 | 2.3963 | Yes | 226668.86 | 54.6998 | GPC EnerSim model | 875 fixtures | Retail Large | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 47889 | GE 10316 - F30T8/CW Straight T8 Fluorescent Tube Light Bulb (http://www.amazon.com/GE-10316-F30T8-Straight-Fluorescent/dp/B0009XCGAA/ref=pd_sim_sbs_hi3) ballast Sylvania 49908 - QTP4X32T8/UNV-ISN-SC-B T8 Fluorescent Ballast (http://www.amazon.com/Sylvania-49908-QTP4X32T8-UNV-ISN-SC-B-Fluorescent/dp/B000V6XRMG/ref=sr_1_1?s=hi&ie=UTF8&qid=1316194058&sr=1-1) | 139259.9069 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -2330.63 | 0 | Medium
328 | T8 Lamp High Performance | baseline is standard T8 fixture | Interior Lighting - C | [8 empty] | Yes |  | 1.1051 | 0.98182 | 1.1256 | 1.1411 | Yes | 58381.2426 | 27.1411 | GPC EnerSim model | 1,018 fixtures | Office | Amusement, Data Center, Education, Government, Grocery, Hospital, Lodging, Medical Office, Office, Religious, Restaurant, Large Retail, Small Office, Small Retail, Warehouse | 48243 | 86 Watt, 96 Inch T8 High Output Cool White Fluorescent Bulb http://www.bulbs.com/espec.aspx?ID=16304&cm_mmc=cse-_-google-_-feed-_-236885&CAWELAID=662958052 | 53604.4598 | 11 | DEER EUL_Summary_10-1-08 | REDACTED | REDACTED | REDACTED | REDACTED | CBECS, Cadmus program experience and research of secondary sources | -300.8109 | 0 | LO_Medium
329 | Industrial: Fan/Efficient Centrifugal Fan | achieve energy savings through improved fan design | Industrial: Fan | [8 empty] | Yes |  | 3.2432 | 0.85563 | 3.7904 | 3.3637 | Yes | 4105.6356 | 0.48874 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 20% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 623.824 | Northwest Power and Conservation Council-Regional Technical Forum data | 2023.1645 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
330 | Industrial: Fan/Fan System Optimization | overall optimization of the fan system including improved system design, enhanced flow design, better maintenance practices, and adjustments to system parameters | Industrial: Fan | [8 empty] | Yes |  | 2.4137 | 0.85563 | 2.821 | 2.5034 | Yes | 4449.5588 | 0.52968 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 7.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 908.4124 | IAC Data (calculated) | 2192.6421 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
331 | Industrial: Fan/High Efficiency Motors | based off of Super Premium motors - at least one efficiency band above NEMA Premium | Industrial: Fan | [8 empty] | Yes |  | 1.9582 | 0.93401 | 2.0965 | 2.0289 | Yes | 2123.1461 | 0.25274 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 1.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 772.4561 | Nexant Calculated | 1512.6024 | 15 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
332 | Industrial: Fan/Improved Controls | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Fan | [8 empty] | Yes |  | 5.4526 | 0.85563 | 6.3727 | 5.6552 | Yes | 4048.9283 | 0.48199 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 6.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 365.9193 | IAC Data (calculated) | 1995.2204 | 10 | PacifiCorp Market Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
333 | Industrial: Fan/Properly Sized Fans | improved matching of fan size to system load | Industrial: Fan | [8 empty] | Yes |  | 5.0159 | 0.85563 | 5.8623 | 5.2023 | Yes | 3056.0883 | 0.3638 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 10.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 300.2371 | IAC Data (calculated) | 1505.9713 | 10 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
334 | Industrial: Fan/Synchronous Belts | Synchronous belts contain grooves that mate with corresponding grooves in the drive sprocket, preventing slip and thus reducing energy losses | Industrial: Fan | [8 empty] | Yes |  | 2.3034 | 0.85563 | 2.6921 | 2.389 | Yes | 448.426 | 0.053381 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet, MECS data, and GPC industrial forecasting data | 1.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 95.9319 | Northwest Power and Conservation Council-Regional Technical Forum data | 220.9742 | 10 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
335 | Industrial: Fan/Paper: Premium Fan | equipment upgrade | Industrial: Fan | [8 empty] | Yes |  | 3.0355 | 0.85563 | 3.5477 | 3.1483 | Yes | 9975.5579 | 1.1875 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 20% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 1619.4087 | Northwest Power and Conservation Council-Regional Technical Forum data | 4915.7296 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
336 | Industrial: HVAC/Equipment Upgrades | Includes upgrades such as packaged air conditioners or heat pumps, chiller plants, condensing units, or other related HVAC equipment | Industrial: HVAC | [8 empty] | Yes |  | 7.2476 | 0.88276 | 8.2101 | 7.5054 | Yes | 26373.312 | 3.7865 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 32.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 2223.7406 | IAC Data (calculated) | 16116.7427 | 12 | PacifiCorp Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
337 | Industrial: HVAC/Improved Controls | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: HVAC | [8 empty] | Yes |  | 10.1978 | 0.84495 | 12.0691 | 10.5676 | Yes | 17437.3019 | 2.5035 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 20.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 877.6975 | IAC Data (calculated) | 8950.5827 | 10 | Nexant Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
338 | Industrial: HVAC/Recommissioning | improved monitoring and verification of building systems | Industrial: HVAC | [8 empty] | Yes |  | 18.717 | 0.84495 | 22.1515 | 19.3957 | Yes | 9275.8594 | 1.3318 | Energy Star Buildings Manual, MECS data, and GPC industrial forecasting data | 5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 254.3842 | IAC Data (calculated) | 4761.3068 | 10 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
339 | Industrial: Lighting/Efficient Lighting (1 shift) | Any changes to overall illumination levels, use of natural lighting, or technology improvements to use more efficient bulbs or ballasts that will decrease the overall lighting energy consumption | Industrial: Lighting | [8 empty] | Yes |  | 16.094 | 1.163 | 13.8385 | 16.5968 | Yes | 3147.3181 | 0 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 19.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 130.9845 | Northwest Power and Conservation Council-Regional Technical Forum data | 2108.061 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
340 | Industrial: Lighting/HighBay Lighting (1 shift) | Any changes to overall illumination levels, use of natural lighting, or technology improvements to use more efficient bulbs or ballasts that will decrease the overall lighting energy consumption | Industrial: Lighting | [8 empty] | Yes |  | 3.704 | 1.163 | 3.1849 | 3.8197 | Yes | 11328.1398 | 0 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 47.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 2048.4872 | Northwest Power and Conservation Council-Regional Technical Forum data | 7587.5424 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
341 | Industrial: Lighting/Lighting Controls (1 shift) | Any changes to overall illumination levels, use of natural lighting, or technology improvements to use more efficient bulbs or ballasts that will decrease the overall lighting energy consumption | Industrial: Lighting | [8 empty] | Yes |  | 5.2272 | 1.163 | 4.4946 | 5.3905 | Yes | 10127.6372 | 0 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 18.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1297.7337 | Nexant Calculated | 6783.4506 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
342 | Industrial: Lighting/Efficient Lighting (2 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 23.3767 | 0.98839 | 23.6512 | 24.1704 | Yes | 1046.415 | 0.21812 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 19.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 25.4811 | Northwest Power and Conservation Council-Regional Technical Forum data | 595.6643 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
343 | Industrial: Lighting/HighBay Lighting (2 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 5.3801 | 0.98839 | 5.4432 | 5.5627 | Yes | 3766.3609 | 0.78506 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 47.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 398.5028 | Northwest Power and Conservation Council-Regional Technical Forum data | 2143.9744 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
344 | Industrial: Lighting/Lighting Controls (2 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 4.4424 | 0.98839 | 4.4946 | 4.5933 | Yes | 10127.6372 | 2.111 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 18.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1297.7337 | Nexant Calculated | 5765.0856 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
345 | Industrial: Lighting/Efficient Lighting (3 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 36.2668 | 0.85563 | 42.3864 | 37.6143 | Yes | 7610.9477 | 0.90602 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 19.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 103.4141 | Northwest Power and Conservation Council-Regional Technical Forum data | 3750.5031 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
346 | Industrial: Lighting/HighBay Lighting (3 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 8.3467 | 0.85563 | 9.7551 | 8.6568 | Yes | 27394.0786 | 3.261 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 47.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1617.3101 | Northwest Power and Conservation Council-Regional Technical Forum data | 13499.184 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
347 | Industrial: Lighting/Lighting Controls (3 shifts) | equipment upgrades and controls | Industrial: Lighting | [8 empty] | Yes |  | 3.8457 | 0.85563 | 4.4946 | 3.9886 | Yes | 10127.6372 | 1.2056 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 18.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1297.7337 | Nexant Calculated | 4990.6709 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
348 | Industrial: Motors Other/High Efficiency Motors | based off of Super Premium motors - at least one efficiency band above NEMA Premium | Industrial: Motors Other | [8 empty] | Yes |  | 2.0291 | 0.9441 | 2.1492 | 2.1008 | Yes | 676.8122 | 0.096736 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 1.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 246.242 | Nexant Calculated | 499.6449 | 15 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
349 | Industrial: Motors Other/Improved Controls | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Motors Other | [8 empty] | Yes |  | 4.9139 | 0.86169 | 5.7027 | 5.093 | Yes | 712.7713 | 0.10188 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 3.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 73.8306 | IAC Data (calculated) | 362.7992 | 10 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
350 | Industrial: Motors Other/Material Handling | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Motors Other | [8 empty] | Yes |  | 1.0893 | 0.86169 | 1.2641 | 1.129 | Yes | 1614.6921 | 0.23079 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 754.529 | Northwest Power and Conservation Council-Regional Technical Forum data | 821.8751 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
351 | Industrial: Motors Other/Material Handling VFD | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Motors Other | [8 empty] | Yes |  | 1.6967 | 0.86169 | 1.969 | 1.7585 | Yes | 6036.232 | 0.86275 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 18.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1810.8696 | Northwest Power and Conservation Council-Regional Technical Forum data | 3072.4303 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
352 | Industrial: Motors Other/Motor Management Plan | number of practices associated with maintaining and operating motors through their entire life cycle, including: developing a repair/replace policy, regularly schedule maintenance, motor standardization, rewind criteria, and design optimization parameters | Industrial: Motors Other | [8 empty] | Yes |  | 7.2072 | 0.86169 | 8.364 | 7.4699 | Yes | 877.9235 | 0.12548 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 2.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 62.0021 | IAC Data (calculated) | 446.8613 | 10 | Engineering Judgement (assumed consistent with NPPC-RTFs management measures) | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
353 | Industrial: Motors Other/Motors Other | includes upgrades not specific pumps or fans, and results in savings from improved motor usage. Motor practice improvements include improved system design, lubrication, and maintenance strategies | Industrial: Motors Other | [8 empty] | Yes |  | 48.4407 | 0.9441 | 51.309 | 50.1528 | Yes | 434.2718 | 0.06207 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 0.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 6.6183 | IAC Data (calculated) | 320.5936 | 15 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
354 | Industrial: Motors Other/Motors: Rewind Large (>100 HP) | involves the rewinding to motors in a controlled environment to minimize or eliminate efficiency losses. Motor rewinds assume rewind techniques consistent with the Green Motors Practices Group™ | Industrial: Motors Other | [8 empty] | Yes |  | 4.0947 | 0.9441 | 4.3372 | 4.2394 | Yes | 14.3607 | 0.0020526 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 0.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 2.5891 | Nexant Calculated | 10.6016 | 15 | PacifiCorp Market Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
355 | Industrial: Motors Other/Motors: Rewind Small (<100 HP) | involves the rewinding to motors in a controlled environment to minimize or eliminate efficiency losses. Motor rewinds assume rewind techniques consistent with the Green Motors Practices Group™ | Industrial: Motors Other | [8 empty] | Yes |  | 2.2556 | 0.9441 | 2.3892 | 2.3354 | Yes | 20.9525 | 0.0029947 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 0.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 6.8574 | Nexant Calculated | 15.4678 | 15 | PacifiCorp Market Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
356 | Industrial: Motors Other/Switch from Belt drive to Direct Drive | improves efficiency through reduction of losses associated with belt drive systems | Industrial: Motors Other | [8 empty] | Yes |  | 2.83 | 0.89926 | 3.147 | 2.9313 | Yes | 478.922 | 0.068452 | Energy Star / DOE ITP Motor Tip Sheet, MECS data, and GPC industrial forecasting data | 7.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 102.4559 | IAC Data | 289.9501 | 12 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
357 | Industrial: Motors Other/Synchronous Belts | Synchronous belts contain grooves that mate with corresponding grooves in the drive sprocket, preventing slip and thus reducing energy losses | Industrial: Motors Other | [8 empty] | Yes |  | 2.3793 | 0.86169 | 2.7612 | 2.466 | Yes | 142.9483 | 0.020431 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet, MECS data, and GPC industrial forecasting data | 1.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 30.581 | Northwest Power and Conservation Council-Regional Technical Forum data | 72.7604 | 10 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
358 | Industrial: Motors Other/Paper: Large Material Handling | equipment upgrade/process improvements | Industrial: Motors Other | [8 empty] | Yes |  | 0.6617 | 0.86169 | 0.76791 | 0.68581 | No
359 | Industrial: Motors Other/Paper: Material Handling | equipment upgrade/process improvements | Industrial: Motors Other | [8 empty] | Yes |  | 0.79177 | 0.86169 | 0.91886 | 0.82063 | No
360 | Industrial: Motors Other/Paper: Premium Control Large Material | equipment upgrade/process improvements | Industrial: Motors Other | [8 empty] | Yes |  | 1.1568 | 0.86169 | 1.3425 | 1.199 | Yes | 2905.6219 | 0.4153 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 18.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 1278.4737 | Northwest Power and Conservation Council-Regional Technical Forum data | 1478.9559 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
361 | Industrial: Other/Bldg Improvements | improvements to the physical plant that result in improved efficiency, productivity, or equipment usage | Industrial: Other | [8 empty] | Yes |  | 5.4483 | 0.93401 | 5.8332 | 5.6449 | Yes | 5118.1859 | 0.60927 | Averaged IAC Data (calculated) & NARC White Paper, MECS data, and GPC industrial forecasting data | 20.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 669.2731 | IAC Data (calculated) | 3646.3721 | 15 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
362 | Industrial: Other/Energy Project Management | Includes the synergistic savings opportunities of plant-wide energy management and improvements across multiple systems such as compressed air, pumping and fan systems | Industrial: Other | [8 empty] | Yes |  | 4.3856 | 0.87451 | 5.015 | 4.5469 | Yes | 5612.6802 | 0.66814 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 29% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 690.8568 | Northwest Power and Conservation Council-Regional Technical Forum data | 3029.8519 | 11 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
363 | Industrial: Other/Integrated Plant Energy Management | Includes the synergistic savings opportunities of plant-wide energy management and improvements across multiple systems such as compressed air, pumping and fan systems | Industrial: Other | [8 empty] | Yes |  | 2.7384 | 0.87451 | 3.1313 | 2.8391 | Yes | 7884.9913 | 0.93864 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 50% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1554.3841 | Northwest Power and Conservation Council-Regional Technical Forum data | 4256.497 | 11 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
364 | Industrial: Other/Plant Energy Management | Includes the synergistic savings opportunities of plant-wide energy management and improvements across multiple systems such as compressed air, pumping and fan systems | Industrial: Other | [8 empty] | Yes |  | 23.5441 | 0.85563 | 27.5168 | 24.4188 | Yes | 2322.4884 | 0.27647 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 12% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 48.6097 | Northwest Power and Conservation Council-Regional Technical Forum data | 1144.4698 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
365 | Industrial: Other/Transformers | Energy efficient transformers that provide improved power quality while minimizing losses | Industrial: Other | [8 empty] | Yes |  | 6.2928 | 1.0242 | 6.1439 | 6.5173 | Yes | 917.5263 | 0.10922 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 1.6% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 160.7042 | Northwest Power and Conservation Council-Regional Technical Forum data | 1011.278 | 30 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
366 | Industrial: Process Air Compressor/Air Compressor Demand Reduction | involve the overall improvement of the compressed air system including improved system design, leak repair, usage practices, more efficient dryer and storage systems, and compressor upgrades | Industrial: Process Air Compressor | [8 empty] | Yes |  | 9.7127 | 0.84797 | 11.454 | 10.0703 | Yes | 10397.2964 | 1.3527 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 15.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 536.2016 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data | 5207.9422 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
367 | Industrial: Process Air Compressor/Air Compressor Equipment | involve the overall improvement of the compressed air system including improved system design, leak repair, usage practices, more efficient dryer and storage systems, and compressor upgrades | Industrial: Process Air Compressor | [8 empty] | Yes |  | 4.7713 | 0.84797 | 5.6268 | 4.947 | Yes | 3748.5322 | 0.48771 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 8.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 393.5203 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data | 1877.6168 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
368 | Industrial: Process Air Compressor/Air Compressor Optimization | involve the overall improvement of the compressed air system including improved system design, leak repair, usage practices, more efficient dryer and storage systems, and compressor upgrades | Industrial: Process Air Compressor | [8 empty] | Yes |  | 4.6374 | 0.84797 | 5.4688 | 4.8081 | Yes | 26925.4615 | 3.5032 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 30.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 2908.2726 | Averaged IAC and Northwest Power and Conservation Council-Regional Technical Forum data | 13486.7991 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
369 | Industrial: Process Air Compressor/High efficiency Compressor motors | involve the overall improvement of the compressed air system including improved system design, leak repair, usage practices, more efficient dryer and storage systems, and compressor upgrades | Industrial: Process Air Compressor | [8 empty] | Yes |  | 2.5252 | 0.92688 | 2.7244 | 2.6155 | Yes | 2069.4812 | 0.26925 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 1.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 593.9731 | Nexant Calculated | 1499.8987 | 15 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
370 | Industrial: Process Air Compressor/Improved Controls | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Process Air Compressor | [8 empty] | Yes |  | 15.5674 | 0.84797 | 18.3584 | 16.1405 | Yes | 15794.0859 | 2.0549 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 18.6% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 508.1893 | IAC Data (calculated) | 7911.161 | 10 | Colorado 2010 DSM Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
371 | Industrial: Process Air Compressor/Motor Management Plan | number of practices associated with maintaining and operating motors through their entire life cycle, including: developing a repair/replace policy, regularly schedule maintenance, motor standardization, rewind criteria, and design optimization parameters | Industrial: Process Air Compressor | [8 empty] | Yes |  | 7.0924 | 0.84797 | 8.364 | 7.3536 | Yes | 3629.7921 | 0.47226 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 2.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 256.3489 | IAC Data (calculated) | 1818.1406 | 10 | Engineering Judgement (assumed consistent with NPPC-RTFs management measures) | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
372 | Industrial: Process Cool/Clean Room: Change Filter Strategy | aim to saving energy through improved clean room equipment and practices | Industrial: Process Cool | [8 empty] | Yes |  | 4.4861 | 0.58022 | 7.7319 | 4.8227 | Yes | 8105.2909 | 1.6895 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 40% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Electronics and Other Electrical Equipment facility type | Chemical_Mfg, Electronic_Equipment_Mfg, Rubber_&_Plastics, | 52.5786 | Northwest Power and Conservation Council-Regional Technical Forum data | 235.875 | 1 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
373 | Industrial: Process Cool/Clean Room: Chiller Optimize | aim to saving energy through improved clean room equipment and practices | Industrial: Process Cool | [8 empty] | Yes |  | 6.9902 | 1.4616 | 4.7824 | 7.2276 | Yes | 8513.1539 | 1.7745 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 14.8% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Electronics and Other Electrical Equipment facility type | Chemical_Mfg, Electronic_Equipment_Mfg, Rubber_&_Plastics, | 693.2604 | Northwest Power and Conservation Council-Regional Technical Forum data | 4846.0524 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
374 | Industrial: Process Cool/Clean Room: Clean Room HVAC | aim to saving energy through improved clean room equipment and practices | Industrial: Process Cool | [8 empty] | Yes |  | 8.9424 | 1.6626 | 5.3786 | 9.2328 | Yes | 5471.0713 | 1.1404 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Electronics and Other Electrical Equipment facility type | Chemical_Mfg, Electronic_Equipment_Mfg, Rubber_&_Plastics, | 635.1463 | Northwest Power and Conservation Council-Regional Technical Forum data | 5679.7625 | 20 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
375 | Industrial: Process Cool/Equipment: Chillers | involves the upgrade of chilling systems providing process cooling | Industrial: Process Cool | [8 empty] | Yes |  | 5.164 | 1.6626 | 3.106 | 5.3316 | Yes | 2898.6723 | 0.6042 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 17.9% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 582.7352 | IAC Data & FinAnswers | 3009.2407 | 20 | DEER data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
376 | Industrial: Process Cool/Improved Controls | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Process Cool | [8 empty] | Yes |  | 0.94435 | 1.5961 | 0.59168 | 0.97525 | No
377 | Industrial: Process Heat/Injection Molding Improvements | Equipment and process improvements to plastic injection molding operations | Industrial: Process Heat | [8 empty] | Yes |  | 0.60846 | 0.80494 | 0.75591 | 0.63123 | No
378 | Industrial: Process Heat/Improved Controls | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Process Heat | [8 empty] | Yes |  | 15.3654 | 0.94704 | 16.2247 | 15.907 | Yes | 36097.9583 | 4.9315 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 30.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1739.7342 | Colorado 2010 DSM Study for Xcel | 26731.7831 | 15 | Colorado 2010 DSM Study for Xcel | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
379 | Industrial: Process Heat/Process Heat O&M | O&M practices on process heating equipment including equipment maintenance, using optimum size and capacity equipment, and developing best-practices guidelines | Industrial: Process Heat | [8 empty] | Yes |  | 1.7737 | 0.62731 | 2.8274 | 1.8537 | Yes | 65388.1906 | 8.933 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 28.6% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 3368.3421 | IAC Data (calculated) | 5974.3241 | 2 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
380 | Industrial: Process Heat/Metal: New Arc Furnace | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Process Heat | [8 empty] | Yes |  | 6.1988 | 0.86507 | 7.1656 | 6.4236 | Yes | 16743.0418 | 2.2873 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 45% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Primary Metals facility type | Primary_Metal_Mfg, | 1380.218 | Northwest Power and Conservation Council-Regional Technical Forum data | 8555.6374 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
381 | Industrial: Process Other/Efficient Agitator | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Process Other | [8 empty] | Yes |  | 6.7984 | 0.86111 | 7.8949 | 7.0464 | Yes | 36225.4955 | 5.084 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 50% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 2710.4072 | Northwest Power and Conservation Council-Regional Technical Forum data | 18426.352 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
382 | Industrial: Process Other/Effluent Treatment System | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Process Other | [8 empty] | Yes |  | 6.8565 | 0.86111 | 7.9624 | 7.1067 | Yes | 7245.0991 | 1.0168 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 15% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 537.4847 | Northwest Power and Conservation Council-Regional Technical Forum data | 3685.2703 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
383 | Industrial: Process Other/Mech Pulp: Premium Process | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Process Other | [8 empty] | Yes |  | 2.2607 | 0.7584 | 2.9808 | 2.3484 | Yes | 198.6966 | 0.027886 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 0.2% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 22.5285 | Northwest Power and Conservation Council-Regional Technical Forum data | 50.9298 | 5 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
384 | Industrial: Process Other/Paper: Efficient Pulp Screen | includes savings from equipment upgrades (such as variable speed drives) as well as energy improvements from enhanced system design or practices | Industrial: Process Other | [8 empty] | Yes |  | 2.811 | 0.86111 | 3.2644 | 2.9136 | Yes | 10867.6487 | 1.5252 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 15% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Paper_Mfg, | 1966.5269 | Northwest Power and Conservation Council-Regional Technical Forum data | 5527.9054 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
385 | Industrial: Process Refrig/Optimization of operating parameters | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Process Refrig | [8 empty] | Yes |  | 2.4058 | 0.65133 | 3.6936 | 2.506 | Yes | 11556.8221 | 1.6948 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 13.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 714.3501 | IAC Data (calculated) | 1718.564 | 3 | Engineering Judgement (consistent with tune-up measures) | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
386 | Industrial: Process Refrig/Adjustable speed drive on compressors | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Process Refrig | [8 empty] | Yes |  | 3.2892 | 0.82157 | 4.0036 | 3.4079 | Yes | 4128.9842 | 0.60553 | PacifiCorp Market Study , MECS data, and GPC industrial forecasting data | 11.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 654.5951 | PacifiCorp Market Study | 2153.101 | 10 | PacifiCorp Market Study | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
387 | Industrial: Process Refrig/Cold Storage Retrofit | Upgrading mechanical equipment responsible for providing cooling to each facility type | Industrial: Process Refrig | [8 empty] | Yes |  | 2.6426 | 0.82157 | 3.2165 | 2.7379 | Yes | 5515.7419 | 0.8089 | Average NPPC-RTF and IAC data, MECS data, and GPC industrial forecasting data | 20.7% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Chemicals facility type | Chemical_Mfg, Electronic_Equipment_Mfg, Miscellaneous_Mfg, | 1088.4235 | Average NPPC-RTF and IAC data | 2876.24 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
388 | Industrial: Process Refrig/Cold Storage Tuneup | Maintaining and enhancing equipment responsible for providing cooling to each facility type | Industrial: Process Refrig | [8 empty] | Yes |  | 3.4231 | 0.65133 | 5.2556 | 3.5658 | Yes | 1625.0621 | 0.23832 | Average NPPC-RTF and IAC data, MECS data, and GPC industrial forecasting data | 15.6% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Chemicals facility type | Chemical_Mfg, Electronic_Equipment_Mfg, Miscellaneous_Mfg, | 70.5949 | Average NPPC-RTF and IAC data | 241.6558 | 3 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
389 | Industrial: Process Refrig/Food: Cooling and Storage | Upgrading mechanical equipment responsible for providing cooling to each facility type | Industrial: Process Refrig | [8 empty] | Yes |  | 3.9725 | 0.82157 | 4.8353 | 4.1158 | Yes | 2401.7835 | 0.35223 | Averaged Council and IAC data, MECS data, and GPC industrial forecasting data | 15.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Food and Kindred Products facility type | Food_Mfg, | 315.2763 | Averaged Council and IAC data | 1252.4346 | 10 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
390 | Industrial: Process Refrig/Food: Refrig Storage Tuneup | Maintaining and enhancing equipment responsible for providing cooling to each facility type | Industrial: Process Refrig | [8 empty] | Yes |  | 3.4231 | 0.65133 | 5.2556 | 3.5658 | Yes | 1121.2118 | 0.16443 | Averaged Council and IAC data, MECS data, and GPC industrial forecasting data | 14.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Food and Kindred Products facility type | Food_Mfg, | 48.7069 | Averaged Council and IAC data | 166.7305 | 3 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
391 | Industrial: Process Refrig/Synchronous Belts | Synchronous belts contain grooves that mate with corresponding grooves in the drive sprocket, preventing slip and thus reducing energy losses | Industrial: Process Refrig | [8 empty] | Yes |  | 2.4375 | 0.82157 | 2.9669 | 2.5255 | Yes | 244.6671 | 0.035881 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet, MECS data, and GPC industrial forecasting data | 1.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 52.3417 | Northwest Power and Conservation Council-Regional Technical Forum data | 127.5842 | 10 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
392 | Industrial: Pump/High Efficiency Motors | based off of Super Premium motors - at least one efficiency band above NEMA Premium | Industrial: Pump | [8 empty] | Yes |  | 1.9921 | 0.92688 | 2.1492 | 2.0633 | Yes | 3898.1745 | 0.50717 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 1.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1418.258 | Nexant Calculated | 2825.2814 | 15 | DEER | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
393 | Industrial: Pump/Improved Controls | upgrades (such as variable speed drives) as well as energy improvements from enhanced monitoring, data collection, and load matching for each system | Industrial: Pump | [8 empty] | Yes |  | 4.0811 | 0.84797 | 4.8128 | 4.2313 | Yes | 35975.5663 | 4.6806 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 30.4% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 4415.4921 | Average IAC and FinAnswers | 18019.9413 | 10 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
394 | Industrial: Pump/Motor rewinds | involves the rewinding to motors in a controlled environment to minimize or eliminate efficiency losses. Motor rewinds assume rewind techniques consistent with the Green Motors Practices Group™ | Industrial: Pump | [8 empty] | Yes |  | 3.0314 | 0.92688 | 3.2705 | 3.1398 | Yes | 110.4035 | 0.014364 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 0.6% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 26.3961 | Nexant Calculated | 80.0172 | 15 | Nexant Calculated | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
395 | Industrial: Pump/Pump Energy Management | involves the overall optimization of the pump system including improved system design, enhanced flow design, better maintenance practices, and adjustments to system parameters | Industrial: Pump | [8 empty] | Yes |  | 7.0924 | 0.84797 | 8.364 | 7.3536 | Yes | 8145.9753 | 1.0598 | Northwest Power and Conservation Council-Regional Technical Forum data, MECS data, and GPC industrial forecasting data | 7.5% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 575.298 | Engineering Judgement (same as motor management plan) | 4080.2692 | 10 | Engineering Judgement | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
396 | Industrial: Pump/Pump Equipment Upgrade | Efficient pumps achieve energy savings through improved pump design and sizing | Industrial: Pump | [8 empty] | Yes |  | 4.795 | 0.84797 | 5.6547 | 4.9716 | Yes | 23509.8378 | 3.0588 | Nexant Calculated, MECS data, and GPC industrial forecasting data | 20% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 2455.8623 | Nexant Calculated | 11775.934 | 10 | Nexant Calculated | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | LO_Slow
397 | Industrial: Pump/Pump System Optimization | involves the overall optimization of the pump system including improved system design, enhanced flow design, better maintenance practices, and adjustments to system parameters | Industrial: Pump | [8 empty] | Yes |  | 2.3156 | 0.88409 | 2.6192 | 2.3994 | Yes | 6539.4714 | 0.85082 | IAC Data (calculated), MECS data, and GPC industrial forecasting data | 12.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 1680.9232 | IAC Data (calculated) | 3892.3504 | 12 | Northwest Power and Conservation Council-Regional Technical Forum data | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
398 | Industrial: Pump/Synchronous Belts | Synchronous belts contain grooves that mate with corresponding grooves in the drive sprocket, preventing slip and thus reducing energy losses | Industrial: Pump | [8 empty] | Yes |  | 2.3414 | 0.84797 | 2.7612 | 2.4276 | Yes | 823.3267 | 0.10712 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet, MECS data, and GPC industrial forecasting data | 1.1% end-use savings at applicable facilities | N/A - savings percentage applied to appropriate NAICS code load forecast. NOTE- Achievable potential reported for this measure is for: Paper and Allied Products facility type | Apparel, Chemical_Mfg, Electronic_Equipment_Mfg, Food_Mfg, Industrial_Machinery, Lumber_Wood_Products, Metal_Fab, Miscellaneous_Mfg, Paper_Mfg, Primary_Metal_Mfg, Rubber_&_Plastics, Stone_Clay_Glass_Products, Textile_Products, Transportation_Equipment_Mfg, | 176.1346 | Northwest Power and Conservation Council-Regional Technical Forum data | 412.3993 | 10 | DOE ITP (Industrial Technologies Program) Motor Tip Sheet | REDACTED | REDACTED | REDACTED | REDACTED | Nexant primary data collection, program experience, and research/compilation of secondary sources | 0 | 0 | Slow
(1) Energy and demand savings for modeled/selected facility type for Commercial facilities, Energy and demand savings for "average" industrial facility, based on GPC forecasting data and percentage savings applied to end-use category
(2) Percentage of non-residential customers for modeled/selected facility type that measure or technology is applicable to, based on market share for the technology and applicability factors (technical feasibility, share for competing measures, measure contribution to end-use kWh consumption)
(3) Forecast of cumulative achievable potential (kWh savings) for an aggressive incentive scenario over period of potential study for all permutations (e.g. new & existing, all heating equipment types) of modeled/selected facility type