### Unit Retirement Study

In the Unit Retirement Study for the 2013 IRP, Georgia Power has conducted economic evaluations for all Georgia Power coal- and oil-fired units.  These economic evaluations compare the costs and benefits of retrofitting, fuel switching, or retiring each of the units considering a suite of currently final, proposed, and/or expected environmental rulemakings and their associated compliance requirements.  This suite includes the final Mercury and Air Toxics Standards (“MATS”) rule, which became effective on April 16, 2012 and requires compliance by April 16, 2015 unless a compliance extension is requested and granted.  In addition, the Company completed evaluations for Plant Boulevard Units 2 and 3 and Plant Bowen Unit 6.  Based on these economic evaluations (along with several other key factors), the Company recommends retirement of sixteen coal- and oil-fired units.  For the remaining coal units, the Company recommends moving forward with compliance investments.

# 2013 Unit Retirement Study

## Introduction

Unit Retirement Study evaluations were performed for each of Georgia Power’s coal- and oil-fired units, as well as for Plant Boulevard Units 2 and 3 and Plant Bowen Unit 6.  For each of the analyses below (Sections 1.6.1-1.6.13), the Unit Retirement Study evaluated controlling or replacing the units based on current and expected compliance requirements, and the results of such analysis were one of the primary determinants in the basis for the Company’s decision to control, fuel switch, retire, or defer action on the unit(s). The set of controls assumed for each unit varies based on what controls are currently required or expected to be required for compliance under current and future environmental rules and regulations.  At the top of each table, there is a list of the controls included in the analysis, along with the year in which the control is assumed to be installed for purposes of the analysis.

As part of the economic analysis, the incremental cost of the controlled steam unit was compared to a proxy replacement unit and a near term reflection of reserve capacity value in cases where the resource balance does not indicate an immediate replacement unit need.  Due to the large number of units facing possible retirement, the year of replacement evaluated for particular units was based on assumed retirements of other units.  The evaluation included hourly production cost modeling and cost implications to the transmission system.  Changes in production cost, capital, and other fixed costs were captured in the comparison to help determine the most economical option for customers.

## Incremental Costs

Incremental costs include fuel, operation and maintenance expenses (“O&M”), maintenance capital, and emissions costs (NOX, SO2, and CO2) associated with continued operation of the facility.  An economic dispatch model was used to forecast fuel costs and emissions costs based on the hourly operation of the unit in each scenario for the years 2013 to 2042.

O&M includes labor, materials, overhead costs, and the costs of engineering and support services requested by the plant.  Maintenance capital costs are the projected capital expenditures necessary to keep the units running through the analysis period at the current or projected level of operation.  For units that will continue under current unit conditions (i.e., no fuel change or significant change in operation hours), five-year projections of unit incremental O&M and maintenance capital costs were obtained from the 2012 budget process along with five years of historical spending data for maintenance capital.  The incremental costs for the remaining years (2018 to 2042) were calculated using an average of the projections for the first 5 years for O&M, along with the last 5 years of actual spending for maintenance capital, and escalating the resulting value at inflation.  For units where operation profiles, fuel types, and/or staffing needs will be significantly impacted by the MATS compliance plan, data was gathered from plant level estimates and/or adjustments were made to the budget information based on sound engineering judgment.  Environmental O&M for all scheduled environmental controls is also included.

Environmental control capital expenditures that are projected to be required for compliance were not included in the ongoing operation capital expenditures described above.  Instead, these incremental capital estimates were provided by Southern Company Services (“SCS”) Engineering and Construction Services (“E&CS”).  The most recently available capital estimates were used in the studies and were included as specified in the analyses below.  The control requirements and dates that are included in the analysis were based on the compliance requirements of currently final, proposed, and/or expected environmental rulemakings and their associated compliance requirements.  As the preliminary or proposed rules are finalized, some of these requirements and dates may shift; however, those included are based on the most recent knowledge and expectations at the time of the analyses.

The combination of these expense streams and the declining revenue requirements on these capital streams constitute the total fixed costs associated with the continued operation for the existing generating units over the 30-year evaluation period.  Additional information about the environmental rulemakings and their projected compliance requirements that are taken into account in the analyses below can be found in the Environmental Compliance Strategy in Technical Appendix Volume 2.

## Replacement Unit Costs

Replacement costs (installation capital, fixed O&M, and continue to operate capital which are all representative of generic, repeatable site-specific estimates) are developed by SCS E&CS.  Fuel transportation costs are estimates from SCS Fuel Services representative of average fuel transportation costs for future units in Georgia.  In addition, individual transmission cost implications of the existing unit retirement and replacement were estimated by SCS Transmission.  For studies where the resource balance shows that a replacement unit would not be needed immediately, a representative capacity value based on historic regression analysis and market data is given to the existing unit.

For the unit retirement studies, units expected to be fueled by coal (Plants Bowen, Branch, Hammond, McIntosh, Scherer, and Wansley) were compared to the expected cost of a generic, repeatable replacement CC sited in Georgia.  For the units that were projected to be fueled primarily by gas or oil (Plants Gaston, Kraft, McManus and Yates), a comparison was made to the expected cost of a generic, repeatable replacement combustion turbine (“CT”) sited in Georgia.  In all comparison studies, the costs of the replacement unit were scaled on a megawatt basis to the same generating capacity as the study unit.  For example, for a 500 MW coal unit retirement study, the costs for a 500 MW portion of a full scale CC would be used for the comparison.

Since Plant Bowen Unit 6 and Plant Boulevard Units 2 and 3 are small CTs that are used exclusively for peaking capacity, they were not compared to a replacement unit but, instead, were compared to a more generic replacement capacity value.

## System Energy Impacts

System energy impact costs were estimated using the Southern Electric System marginal replacement costs for both continued unit operation and the replacement unit alternative.  Marginal replacement costs were generated with the PROSYM® model over a 30-year period (2013 to 2042).  The marginal replacement costs were then used to dispatch both the coal unit and the replacement unit.  The energy benefits (marginal replacement costs minus variable operating costs) were compared to determine the energy value to the Southern Electric System for both generating options.  The net present value of the difference between the replacement unit’s energy impact and the existing unit’s energy impact were calculated to determine the overall net contribution to system energy costs.

## Scenarios

Uncertainty is a challenge for planning.  The Company works to manage this challenge by considering multiple different future outcomes in key areas of uncertainty, including future CO2 emissions price and future natural gas markets.  The Company formally analyzes multiple scenarios, each of which adopts a particular view of future CO2 emissions price and a particular view of future natural gas markets.

With its scenario modeling consultant, Charles River Associates (“CRA”), the Company developed three possible future CO2 views and three possible future natural gas market views.  The scenarios created by the combination of these CO2 views and natural gas views were developed to represent a range of plausible outcomes.  Each of the nine scenarios provides an internally-consistent view of fuel, electricity and other markets in the US economy.  For each of these scenarios, the Company has performed the detailed asset valuation analysis for each unit discussed in this filing.

Three future CO2 emission price views were considered.  Each was defined by a different future path of the price of CO2.  The Existing CO2 regulation view does not place a price on carbon emissions; however it does constrain all future new coal generation built in the U.S. to include only advanced carbon capture and sequestration technology.  The Moderate CO2 price view assumes a $10 per metric ton price (REDACTED) of CO2 beginning in 2017 and escalates this price at REDACTED above inflation.  The Substantial CO2 price view adds a more onerous $20 per metric ton price of CO2 (REDACTED) beginning in 2020.  This CO2 price also escalates at REDACTED above inflation.  These CO2 price levels were chosen to span the plausible short term and long term range of CO2 requirements when considering multiple factors, including U.S. economic impact and likely cost-containment provisions.

Three future natural gas market views were considered.  They reflect different assumptions about the future supply and demand of natural gas in North America. Differences in supply assumptions largely reflect uncertainty in the future cost and volume of gas production, especially from shale sources.  Differences in demand assumptions largely reflect uncertainty in the future magnitude of growth in domestic industrial gas consumption and in the future magnitude of natural gas for LNG export.  These result in three different price futures for U.S. natural gas – lower, moderate and higher.

The modeling system that CRA employs for the Company's analyses (MRN-NEEM) is a sophisticated, multi-sector dynamic general equilibrium model of the U.S. economy that takes into account supplies and demands for all goods and services in the economy, focusing on the markets for energy and energy-intensive goods and services—especially electricity.  The model finds price paths in all markets so that the quantity supplied is equal to the quantity demanded.  Feedbacks among all of these markets are considered in generating a fully integrated analysis of each scenario.

In each scenario, the modeling captures shifts in generation investment choices through retirements of some existing capacity (primarily low capacity factor coal), retrofit of other existing capacity with emission control and other equipment, fuel switching of some units, and the construction of new generating capacity.  Scenarios with higher CO2 and fuel costs generally have higher electricity prices, reduced growth in overall U.S. economic activity and reduced growth in electricity sales.  All of these interrelated factors, including reductions to load growth, are considered in the Company’s scenario modeling process.

The detailed asset evaluations also incorporated the nine fully integrated scenarios in order to capture variations in the operating environments that may affect the economic value of the units.  See Technical Appendix Volume 1 for more details on scenario planning.

## Summary of Study Results

The following tables (Sections 1.6.1-1.6.13) represent the NPV customer cost results for the comparison of costs of the appropriate replacement proxy unit minus the cost to continue to operate each set of coal/oil/gas units with the controls listed for that particular unit.  When a positive value is given for a scenario, the NPV of costs for the replacement generation are greater than the NPV costs for controlling the existing unit; therefore, the existing unit is the better economic option.  Appendix A summarizes the environmental costs applied to each of the controlled units.  Table A.1 provides the in-service cost of the individual environmental controls.  In Table A.2, the NPV of the declining revenue requirements (“DRR”) for each of these controls is provided.  The tabular data from Table A.2 can be used to adjust the controls assumptions included in the analysis presented in sections 1.6.1 - 1.6.11.  If the analysis was to be examined without a particular environmental control that was included in the results given in Sections 1.6.1-1.6.11, the NPV of the DRR for that particular control could be added back to each scenario.  Conversely, if there is an additional required control that was not included in the results in Sections 1.6.1-1.6.11, the NPV for the DRR for that control would be subtracted from each cell in the matrix.

Appendix B summarizes the costs and benefits of continued operation for each set of coal- and oil-fired units for the Existing CO2 – Moderate Fuel case over the 30-year period (2013-2042).

1.6.1 Plant Bowen Units 1-4

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2014-2015 ACI, FGD Additive, SAMC (U1-2) ~ 2014-2015 ESP Mods (U1-2) ~ 2015-2016 CEMS ~ 2016 Baghouse, ACI, FGD Additive, SAMC (U3-4) ~ 2016-2017 Scrubber Waste Water Treatment ~ 2017 316(b) Studies ~ 2017-2019 Dry Bottom Ash ~ 2017-2031 Landfill ~ 2018 Low Vol WWT ~ 2020 Intake Screens

Table 1.1

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Bowen, it has been determined that baghouses with Activated Carbon Injection (“ACI”), Flue Gas Desulfurization Scrubber (“FGD”) Additives, Sulfuric Acid Mist Control (“SAMC”), and mercury Continuous Emissions Monitoring Systems (“CEMS”) are required on Units 3-4 for compliance with MATS, whereas Bowen Units 1-2 will comply with MATS using ACI, FGD Additives, SAMC, along with CEMS and Electrostatic Precipitator (“ESP”) Modifications. For compliance with EPA’s Coal Combustion Residuals (“CCR”) Rule it is assumed that a conversion to a Dry Bottom Ash system will be required for all four units due to anticipated requirements to close the ash pond.  The CCR Rule is also assumed to require modifications to the landfill for all four units at Bowen for disposal of ash and gypsum. It is assumed that Steam Electric Effluent Guidelines revisions will require additional scrubber waste water treatment.  In addition, the Steam Effluent Guidelines are assumed to require installation of a Low Volume Wastewater Treatment (“WWT”) system once the ash pond is closed due to the CCR rule.  It is further assumed that the 316(b) rule will require new water intake structure screens to be installed for all four units.

1.6.2 Plant Branch Units 3 & 4

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2016 FGD, SCR, ACI, FGD Additive & SAMC~ 2016 CEMS ~ 2016-2017 Dry Fly Ash ~ 2017 Dry Bottom Ash ~ 2018 Gypsum Dewatering ~ 2017-2031 Landfill ~ 2018 Low Vol WWT ~ 2020 Scrubber Wastewater Treatment  ~ 2019 316(b) Studies ~ 2021 Intake Structures

Table 1.2

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Branch Units 3-4, the assumed costs include a FGD and a selective catalytic reduction unit (“SCR”) required by the Georgia Multipollutant Rule.  It is assumed that Branch 3-4 can comply with MATS by installing ACI, FGD Additives, SAMC, and mercury CEMS.  The assumed controls for Branch 3-4 required for compliance with EPA’s CCR Rule include a conversion to a Dry Fly Ash and Dry Bottom Ash system and modifications to the landfill for disposal of ash and gypsum.  It is assumed that the steam effluent guidelines revisions will require systems for Gypsum Dewatering and Low Volume WWT once the ash pond closure is required by the CCR rule.  A system for Scrubber Wastewater Treatment is also assumed to be required by the steam effluent guidelines revisions.  Finally, new water intake structures are assumed to be needed due to the 316(b) rule.  REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED.

1.6.3 Plant Gaston Units 1-4

2015 Compliance Results

Customer Costs for Replacement CT (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation for GPC’s Ownership Share of Gaston 1-4

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2016 Primary Fuel Switch~ 2017 Low Vol WWT  ~ 2019 316(b) Study ~ 2019 Intake Screens ~ 2021 Cooling Tower

Table 1.3

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Gaston Units 1-4, fuel switching of the units to burn natural gas as the primary fuel is the most cost-effective MATS compliance option.  This includes the cost for a gas lateral to the plant.  Coal will be maintained as a backup fuel supply until compliance with the pending CCR rule or other rules limiting use of coal is required.  It is assumed that once EPA’s CCR Rule is effective that closure of the existing ash pond will be required.  At this point, this analysis assumes that Gaston 1-4 will require a Low Volume WWT system in order to comply with the requirements in the steam effluent guideline revisions.  The assumption for compliance with the 316(b) rule in this analysis for Gaston 1-4 includes both new water intake screens and cooling towers.

1.6.4 Plant Hammond Units 1-4

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2014-2015 ACI, FGD Additive and SAMC~ 2014 ESP Mods ~ 2014-2015 CEMS ~ 2018 SNCR (U1-3) ~ 2018 Dry Bottom Ash ~ 2019 Low Vol WWT ~ 2019-2032 Landfill ~ 2019 Cooling Tower ~ 2019 Intake Structures & 316(b) Studies ~ 2021 Scrubber Wastewater Treatment

Table 1.4

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Hammond, ACI, FGD Additives, SAMC, and CEMS, as well as ESP Modifications will be necessary to comply with the MATS rule. Selective Non-Catalytic Reduction units (“SNCRs”) (Units 1-3) are assumed to be required for compliance with future Ozone National Ambient Air Quality Standards.  For compliance with EPA’s CCR Rule it is assumed that a conversion to a Dry Bottom Ash system and landfill modifications will be required for all four units.  The CCR Rule is also assumed to require closure of ash ponds at which time it is assumed that a Low Volume WWT system and a Scrubber Wastewater Treatment system will be required to comply with the steam effluent guideline revisions.  It is further assumed that closed cycle cooling towers with associated modifications to the intake structure will be required to address both the dissolved oxygen Total Maximum Daily Load (“TMDL”) issue as well as the new 316(b) intake structure rule.  REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED.

1.6.5 Plant Kraft 1-4

2015 Compliance Results

Customer Costs for Replacement CT (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2015 Fuel Switch  to #2 Oil ~ 2017 Low Vol WWT ~ 2019 316(b) studies ~ 2019 Intake Screens ~ 2021 Cooling Tower

Table 1.5

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

In this analysis, a conversion to #2 oil is the most economic option for Units 1-3 to comply with the MATS rule.  As noted in the Amended Application filed as part of the 2011 IRP Update in Docket No. 34218, based on current regional fuel forecasts, an adequate supply of non-firm natural gas is not expected to be available during summer and winter peak hours when needed and firm natural gas transportation is not cost effective, thus eliminating natural gas operation at Plant Kraft as a reliable generation option in the future.  It is assumed that Unit 4 will be required to convert from #6 oil to #2 oil to comply with the SO2 NAAQS.  In addition, as oil-fired units, Units 1-4 are limited to an 8% capacity factor limit to comply with the MATS rule.  Compliance with EPA’s CCR Rule is assumed to require closure of the ash pond at which time a Low Volume WWT system will be required to comply with the steam effluent guideline revisions.  Finally, compliance with the 316(b) rule is assumed to require new water intake screens and a cooling tower.

1.6.6 Plant McIntosh 1

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the unit:

- 2016 Fuel Switch ~ 2016 ACI & DSI ~ 2017 Dry Bottom Ash ~ 2017 316(b) Studies ~ 2018 SNCR ~ 2016 CEMS ~ 2018 Low Vol WWT ~ 2018-2032 Landfill ~ 2019 Intake Structures

Table 1.6

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For McIntosh Unit 1, the most economic option to comply with the MATS rule requirements includes a fuel switch to burn PRB coal and the addition of ACI and Dry Sorbent Injection (“DSI”) systems.     It is assumed that compliance with EPA’s CCR Rule will require closure of the ash ponds and thus the addition of a Dry Bottom Ash system and landfill modifications.  At the time of the ash pond closure, it is assumed that a Low Volume WWT system will be required to comply with steam effluent guideline revision requirements.  The 316(b) rule is assumed to require McIntosh to incur costs for new water intake structures.

1.6.7 Plant McManus 1-2

2015 Compliance Results

Customer Costs for Replacement CT (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2017 Switch to #2 Oil  ~ 2017 316(b) Studies ~ 2018 Low Vol WWT ~ 2019 Intake Screens ~ 2021 Cooling Tower

Table 1.7

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

In this analysis, it is assumed that a conversion to #2 oil will be required to comply with the SO2 NAAQS.  In addition, as oil-fired units, Units 1 and 2 are limited to an 8% capacity factor limit to comply with the MATS rule.  Compliance with EPA’s steam effluent guideline revisions is assumed to require installation of a Low Volume WWT system, and compliance with the 316(b) rule is assumed to include new water intake screens and a cooling tower.

1.6.8 Plant Scherer 1-3

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation for GPC’s Ownership Share of Scherer 1-3

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2015 Bromine Injection & CEMS ~ 2017 316(b) Study ~ 2017-2018 Dry Fly Ash ~ 2018-2019 Dry Bottom Ash ~ 2019 Low Vol WWT ~ 2019 Gypsum Dewatering ~ 2019-2032 Landfill ~ 2020 Intake Screens ~ 2021 Scrubber WWT

Table 1.8

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

Plant Scherer Units 1-3 are already equipped with FGDs, SCRs, baghouses, and activated carbon injection.  It is assumed Units 1-3 will be able to more cost effectively comply with MATS using a Bromine Injection system and that updates to mercury CEMS equipment will be required. For compliance with EPA’s CCR Rule it is assumed that a conversion to a Dry Fly Ash system, Dry Bottom Ash system, and modifications to the landfill will be required for each unit.   It is assumed that the steam effluent guideline revisions will require installation of a Low Volume WWT system, a Gypsum Dewatering system, and a Scrubber Wastewater Treatment system.  It is also assumed that new water intake screens will be required by the 316(b) rule.

1.6.9 Plant Wansley 1-2

2015 Compliance Results

Customer Costs for Replacement CC (REDACTED In-Service) proxy Relative to the Cost of Continued Operation for GPC’s Ownership Share of Wansley 1-2

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2014 ACI, SAMC, & ESP Mods ~ 2014-2015 FGD Additive ~ 2015 CEMS ~ 2016-2017 Dry Fly Ash ~ 2017 316(b) Studies ~ 2017-2018 Dry Bottom Ash ~ 2018 Low Vol WWT ~ 2019-2031 Landfill ~ 2019-2020 Gypsum Dewatering ~ 2020 Intake Screens ~ 2021 Scrubber WWT

Table 1.9

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

The plan for Plant Wansley Units 1-2 is to install ACI, FGD Additives, SAMC, along with CEMS and ESP Modifications for compliance with the MATS rule. For compliance with EPA’s CCR Rule it is assumed that a conversion to a Dry Fly Ash system, a Dry Bottom Ash system, and modifications to the landfill will be required for both units.  The steam effluent guidelines revisions are assumed to require a Low Volume WWT system, a Gypsum Dewatering system, and a Scrubber Wastewater Treatment system. It is also assumed that new water intake screens will be required for both units by the 316(b) rule.

1.6.10 Plant Yates 1-5

2015 Compliance Results

Customer Costs for Replacement CT (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2015 Primary Fuel Switch ~ 2018 Low Vol WWT ~ 2017 316(b) Studies

Table 1.10

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Yates 1-5, conversion to burn natural gas as the primary fuel is the most cost-effective option because of the MATS rule requirements.  For compliance with EPA’s steam effluent guideline revisions, it is assumed that Yates 1-5 will require a Low Volume WWT system after closure of the ash pond is required due to the CCR Rule.

1.6.11 Plant Yates 6-7

2015 Compliance Results

Customer Costs for Replacement CT (REDACTED In-Service) Proxy Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the units:

- 2015 Primary Fuel Switch ~ 2017 Low Vol WWT ~ ~ 2017 316(b) Studies ~ 2019 316(b) Intake Screens

Table 1.11

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 | Moderate CO2 | Substantial CO2 |
| --- | --- | --- | --- |
| High Fuel | REDACTED | REDACTED | REDACTED |
| Moderate Fuel | REDACTED | REDACTED | REDACTED |
| Low Fuel | REDACTED | REDACTED | REDACTED |

For Plant Yates 6-7, conversion of the units to burn natural gas as the primary fuel is the most cost-effective option because of the requirements of the MATS rule and the Georgia Multipollutant Rule.  Coal will be available as a backup fuel supply until compliance with the pending CCR rule or other rules limiting use of coal is required.  For compliance with EPA’s steam effluent guidelines revisions, it is assumed that Yates 6-7 will require a Low Volume WWT system once the ash pond is closed due to the CCR Rule.  The assumption for compliance with the 316(b) rule for Yates 6-7 includes new water intake screens.

1.6.12 Plant Boulevard 2 & 3

Customer Costs for Generic Replacement Cost (REDACTED In-Service) Relative to the Cost of Continued Operation

NPV (2013-2042) in Millions of Dollars

- In-Service Dates of Environmental Controls included on the unit:

None needed as these are oil-fired CT units.

Table 1.12

| Mid-Year 30-yr NPV 2013 $M | Existing CO2 |
| --- | --- |
| Moderate Fuel | REDACTED |

Plant Boulevard Units 2 & 3 are oil-fired CTs rated at a capacity of 14 MW each, and were installed in 1970 along with Unit 1.  The economic evaluation in Table 1.12 provides the NPV for customers over a 30-year study period and includes an estimated cost of repair that is based on damage observed by camera probe inspections.

In addition, the Company completed a comparison of Units 2 & 3 Continue to Operate Capital and O&M costs to the replacement capacity costs over the next 10 years (2013-2022).  That analysis showed that the CT had a value of approximately REDACTED in a Moderate Existing scenario.  The units would have to continue operation, without an additional failure, for approximately REDACTED more years in order to break even economically for customers after the repairs.

Boulevard Unit 1 is not damaged and remains a cost-effective unit for customers, and therefore, is recommended for continued operation.

1.6.13 Plant Bowen 6

Customer Costs for Generic Replacement Cost (REDACTED In-Service) Relative to the Cost of Continued Operation

NPV (2013-2042) Dollars

- In-Service Dates of Environmental Controls included on the unit:

None needed as this is an oil-fired CT unit.

Table 1.13

| Mid-Year 30-yr NPV 2013 $ | Existing CO2 |
| --- | --- |
| Moderate Fuel | REDACTED |

For the Plant Bowen Unit 6 analysis, the Unit 6 Continue to Operate Capital and O&M costs were compared to the replacement capacity costs over the next 30 years (2013-2042).  This analysis showed that the CT had a value of approximately REDACTED in a Moderate Existing scenario.

Appendix A: Environmental Controls 
Table A.1

In-Service Dollars for Environmental Controls

* Ownership dollars only shown

Table A.1 (Continued)

In-Service Dollars for Environmental Controls

* Ownership dollars only shown

Table A.2

NPV of the Revenue Requirements for Environmental Controls

* Ownership dollars only shown

Table A.2 (Continued)

NPV of the Revenue Requirements for Environmental Controls

* Ownership dollars only shown

Appendix B
Existing CO2 – Moderate Fuel

NPV (2013-2042) in Millions of Dollars

Appendix B
Existing CO2 – Moderate Fuel

NPV (2013-2042) in Millions of Dollars

Appendix B
Existing CO2 – Moderate Fuel

NPV (2013-2042) in Millions of Dollars