GEORGIA POWER COMPANY

Docket No. 36989

Georgia Power Company’s 2016 Annual Surveillance Report

Staff Data Request No. STF-34

STF-34-10

Question:

When was this underground circuit installed? How often is the equipment inspected? List the date of the last inspection.

Response:

Georgia Power’s response below is based on the information it has gathered and reviewed to date.  Its investigation is ongoing, and Georgia Power reserves the right to supplement or amend this response.

Between February 1985 and November 1988, a network underground system was installed from the existing substation to another substation to serve the Main Terminal and Concourses A-D.

Between September 1993 and May 1994, as part of the construction of Concourse E, the underground system was extended to serve Concourse E.

Between November 2001 and June 2002, an additional cable was added to the existing network underground system between two substations.

Between March 2004 and December 2007, a new cable network underground system was installed to serve the new International Terminal (Concourse F).

Georgia Power typically performs a visual inspection and an infrared scan of the equipment in the underground tunnel at the Airport approximately every 12-18 months.

The last infrared scan of the equipment in the underground tunnel prior to December 17, 2017 was performed on June 17, 2016.  The last visual inspection of equipment in the underground tunnel prior to December 17, 2017 was on November 14, 2017.

Since the outage on December 17, 2017, Georgia Power has performed a thorough visual and infrared inspection of the equipment in the underground tunnel at the Airport.

Contact:  Richard Dodd