GEORGIA POWER COMPANY

Docket No. 36989

Georgia Power Company’s 2016 Annual Surveillance Report

Staff Data Request No. STF-34

STF-34-7

Question:

List equipment that malfunctioned and/or was involved in the outage. Please identify the last time the equipment that failed was inspected by Georgia Power. What were the inspection procedures?

Response:

Georgia Power is in the process of conducting a thorough investigation into the cause of the power outage at the Hartsfield-Jackson Atlanta International Airport on December 17, 2017, including the malfunction of any equipment and will provide information from that investigation as soon as it is able to.

Georgia Power’s response below is based on the information it has gathered and reviewed to date.  Its investigation is ongoing, and Georgia Power reserves the right to supplement or amend this response.

The fire in the underground tunnel at the Airport damaged two vacuum switches and multiple cables.  Prior to the December 17, 2017 incident, Georgia Power last performed a visual inspection of that equipment on November 14, 2017, and the last infrared scan of that equipment on June 17, 2016.

Attachment STF-34-7 is a copy of Georgia Power’s Network Underground Operations and Test Procedures, OTP No. 25, Inspection, Cleaning, and Maintenance of Manholes, Vaults, and Equipment. The attachment is trade secret and has been redacted in its entirety for public disclosure purposes.

Contact:  Richard Dodd