GEORGIA POWER COMPANY

Docket No. 36989

Georgia Power Company’s 2016 Annual Surveillance Report

Staff Data Request No. STF-34

STF-34-8

Question:

Was there a back-up system available to be switched over to in case one circuit failed? If so, Why was a back-up / redundant not able to pick up load? If not, please explain why no back or redundant system had been installed.

Response:

Georgia Power is in the process of conducting a thorough investigation into the cause of the power outage at the Hartsfield-Jackson Atlanta International Airport (“Airport”) on December 17, 2017 and will provide information from that investigation as soon as it is able to.

Georgia Power’s response below is based on the information it has gathered and reviewed to date.  Its investigation is ongoing, and Georgia Power reserves the right to supplement or amend this response.

The Georgia Power power delivery system that serves the Main Terminal and Concourses A-F at the Airport is a network underground system with redundancy. The network underground system is served by two substations and includes two network systems, each of which is designed to serve its full load even with one circuit out. Please see the Company’s response to STF-34-2 for additional information.

Georgia Power understands that the Airport has its own on-site independent emergency generation.  Georgia Power does not operate the Airport’s independent emergency generation.

Contact:  Richard Dodd