BEFORE THE

PUBLIC SERVICE COMMISSION

OF THE

STATE OF GEORGIA

PRE-FILED REBUTTAL TESTIMONY

OF INTERVENOR,

NESTLE PURINA PETCARE COMPANY

PSC DOCKET NO. 42509

GEORGIA POWER COMPANY, PETITIONER

v.

WALTON ELECTRIC MEMBERSHIP CORPORATION, RESPONDENT

and

NESTLE PURINA PETCARE COMPANY, INTERVENOR

PRE-FILED REBUTTAL TESTIMONY FROM RYAN MONTGOMERY ON BEHALF OF INTERVENOR NESTLE PURINA PETCARE COMPANY

| ### BEFORE THE PUBLIC SERVICE COMMISSION STATE OF GEORGIA |  |
| --- | --- |
| GEORGIA POWER COMPANY, Petitioner, v. THE WALTON ELECTRIC MEMBERSHIP CORPORATION, Respondent, NESTLE PURINA PETCARE COMPANY, Intervenor. | DOCKET NO. 42509 |

PRE-FILED REBUTTAL TESTIMONY FROM RYAN MONTGOMERY ON BEHALF OF INTERVENOR NESTLE PURINA PETCARE COMPANY

PLEASE STATE YOUR NAME AND OCCUPATION

A.	My name is Ryan Montgomery, and I am the Electrical and Control Engineering Manager for Nestle Purina North America and have been since April of 2018.

Q.	ARE YOU THE SAME RYAN MONTGOMERY THAT SUBMITTED DIRECT TESTIMONY ON BEHALF OF NESTLE PURINA PETCARE COMPANY ON AUGUST 9, 2019?

A.	Yes, I am.

Q.	WHAT IS THE PURPOSE OF THIS ADDITIONAL TESTIMONY?

A.	I am responding to certain portions of the testimony of Cliff Bishop, Harold D. Lawson, Glenn W. Dyke, and John D. Osteraas.

Q.	MR. LAWSON TESTIFIED THAT “BOTH OWNERS WERE AND ARE USING ELECTRICAL POWER SUPPLIES OF 480V, 3 PHASE, 60 HERTZ AS WELL AS 277 VOLT FOR LIGHTING.”  (Lawson Test., Exhibit HDL-2)  IS THAT ANALYSIS CORRECT?

A.	No, Mr. Lawson fails to recognize that in addition to electrical power supplies of 480V, 3 Phase, 60 Hertz and 277V for lighting, Nestle Purina will also be using 5kV VFDs and motors for eight large process equipment motors.  Nestle Purina’s new 5kV substation will directly supply Nestle Purina’s new 5kV VFDs located in a new electrical room via new underground conduit.  The existing underground conduit has not been reused because the original facility’s electrical equipment was not capable of supplying power at 5KV to support these motors.

Q.	MR. LAWSON TESTIFIED THAT NESTLE PURINA REUSED THE LIGHTING WIRE AND CONDUIT IN THE MANUFACTURING AREA, SPECIFICALLY “LIGHTING CHANGES BY NESTLE PURINA IS THE SAME TYPE LIGHTING NEEDED IN THE SPRINGS INDUSTRIES, INC. FACILITY”.  (Lawson Test., Exhibit HDL-2) IS THAT ANALYSIS CORRECT?

A.	No, the original lighting fixtures were obsolete, did not meet Nestle Purina’s lighting standards for efficiencies, hygienic design, Lumen levels, materials of construction or explosion ratings required for the specific, different use of our process area.  As a result, Nestle Purina has installed all new wiring and wire basket for all of the new LED lighting fixtures.  Moreover, the original light fixtures were not adequate to provide a safe working condition for factory personnel or for food safety in open product areas as many of the fixtures contained glass and were not sealed properly for wet environments and insect harboring.  Nestle Purina’s pet food process also requires a dry ingredients process area, which carries a classification of Class II, Division 2, Group G, and requires light fixtures that are appropriately rated for combustible dust.  All new light fixtures were also installed in the warehousing area.

Q.	I AM HANDING YOU WHAT HAS BEEN MARKED AS EXHIBIT MONTGOMERY-2.  WHAT IS IT?

A.	This is a series of photographs showing Nestle Purina installed all new conduit between the new packaging substation and the area known as MCC7.  Nestle Purina installed over fifty new underground conduits.

Q.	DO THESE PHOTOGRAPHS ACCURATELY REPRESENT THE NEW CONDUIT AS YOU REMEMBER?

A.	Yes.

Q.	DID GEORGIA POWER HAVE THE CAPACITY TO SERVE NESTLE PURINA’S FACILITY?

A.	Georgia Power did not leave us feeling comfortable that they would be able to supply Nestle Purina with the necessary power.  This concern is evidenced by email correspondence attached to Mr. Dyke’s testimony (GWD-6/NPCC0000174).  In email correspondence dated February, 21, 2019, sent by Shelby Rae Holsomback Georgia Power indicated that as long as no new loads moved into the industrial park then Georgia Power could supply Nestle Purina up to 9.9MW as a short term solution.  Nestle Purina had concerns about what would happen if a new or existing customer required and contracted additional power, which would have reduced Georgia Power’s ability to supply the Hartwell Facility.  Additionally, Georgia Power indicated that it would take twelve months to complete the construction of a new transmission substation on our property.

Q.	I AM HANDING YOU WHAT HAS BEEN MARKED AS EXHIBIT MONTGOMERY–3.  DO YOU RECOGNIZE THESE EMAILS?

A.	Yes, the email is from Laurie Ewbank to Shelby Holsomback describing a spreadsheet that contained Nestle Purina’s anticipated factory loading based on the design and vendor data.  In the body of the email Laurie Ewbank highlights the fact that Nestle Purina continued to update and adjust our loads as Nestle Purina continued to finish the design and receive information from vendors.

Q.	I AM HANDING YOU WHAT HAS BEEN MARKED AS EXHIBIT MONTGOMERY-4.  DO YOU RECOGNIZE THIS DOCUMENT?

A.	Yes, this is a spreadsheet showing Nestle Purina’s estimated loading for the Hartwell Facility.  This was attached to Laurie Ewbank’s email described above.  The estimated loading excluded wastewater and existing infrastructure, but included Process and Packaging for Line 1 & 2, the area known as Variety Pack, Boilers, and Compressors.

Q.	I AM HANDING YOU WHAT HAS BEEN MARKED AS EXHIBIT MONTGOMERY-5.  DO YOU RECOGNIZE THIS DOCUMENT?

A.	Yes, this is a portion of a spreadsheet showing Nestle Purina’s estimated loading for the Hartwell Facility after adding Process and Packaging for Line 3 and the new Phase II building expansion.

Q.	WHAT OTHER ELECTRICAL CHANGES WERE NECESSARY TO ACCOMMODATE NESTLE PURINA’S PROCESSES?

A.	Nestle Purina’s manufacturing process requires that the majority of the motors are controlled by Variable Frequency Drives ("VFDs”).  The VFDs are installed in most of the new motor control center equipment that was purchased by Nestle Purina.  The original electrical equipment did not contain the VFDs necessary to control or run Nestle Purina’s process.

Q.	I AM HANDING YOU WHAT HAS BEEN MARKED AS EXHIBIT MONTGOMERY-6.  DO YOU RECOGNIZE THIS DOCUMENT?

A.	Yes, this table summarizes the approximate equipment and installation costs of Nestle Purina’s major electrical equipment.  This table does not include the cost of the thousands of controls instrumentation (i.e. flow meters, temperature transmitters, level transmitters, weight transmitters, control valves, safety devices, etc.) as it is difficult to separate the individual instrumentation cost from the total cost of the vendor equipment that it was installed on.

Q.	MR. DYKE TESTIFIED THE “CHARACTER OF THE SERVICE IS PERMANENT SERVICE.” (Dyke Test., p. 9, ln. 30)  IS THAT ANALYSIS CORRECT?

A.	No, in fact, Georgia Power admits that Nestle Purina only had temporary power.  This is indicated in email correspondence sent from Shelby Rae Holsomback dated February 18, 2019 (GWD-6/NPCC0000169).  Specifically, Ms. Holsomback writes, “We would also like to talk through additional details of how this project will continue to progress forward and hope to be able to provide updated timelines on where we stand in delivering a final proposal for permanent service to the facility.”

Q.	MR. BISHOP TESTIFIED REGARDING ANY ADDITIONS MR. BISHOP OBSERVED TO THE FACILITY.  (Bishop Test., p. 4, lns. 6-11)  DOES MR. BISHOP’S TESTIMONY ACCURATELY REPRESENT ADDITIONS TO THE FACILITY?

A.	No, Mr. Bishop made no reference to the new 100,000 square foot expansion building that is currently under construction which will house production lines three and four.

Q.	MR. DYKE TESTIFIED REGARDING ANY ADDITIONS MR. DYKE OBSERVED TO THE FACILITY.  (Dyke Test., p. 7, lns. 7-14)  DOES MR. DYKE’S TESTIMONY ACCURATELY REPRESENT ADDITIONS TO THE FACILITY?

A.	No, similar to Mr. Bishop, Mr. Dyke fails to reference the new 100,000 square foot expansion building that is currently under construction which will house production lines three and four.  The new 100,000 square foot expansion building can clearly be seen in Photo-3, Dyke Test., p. 8.

| ### BEFORE THE PUBLIC SERVICE COMMISSION STATE OF GEORGIA |  |
| --- | --- |
| GEORGIA POWER COMPANY, Petitioner, v. THE WALTON ELECTRIC MEMBERSHIP CORPORATION, Respondent, NESTLE PURINA PETCARE COMPANY, Intervenor. | DOCKET NO. 42509 |

# CERTIFICATE OF SERVICE

I hereby certify that the foregoing PRE-FILED REBUTTAL TESTIMONY FROM RYAN MONTGOMERY	ON BEHALF OF INTERVENOR NESTLE PURINA PETCARE COMPANY in the above-referenced docket was filed with the Commission's Executive Secretary, an electronic copy of same was served upon all parties and persons listed below via electronic mail, or unless otherwise indicated, as follows:

| Reece McAlister* Executive Secretary Georgia Public Service Comm. 244 Washington Street, SW Atlanta, GA 30334 reecem@psc.state.ga.us |  | Nancy G. Gibson Georgia Public Service Comm. 244 Washington Street, SW Atlanta, GA 30334 ngibson@psc.state.ga.us |  | Robert P. Edwards, Jr. William N, Droze Troutman Sanders LLP 600 Peachtree Street, N.E. Atlanta, Georgia 30308 bob.edwards@troutman.com |
| --- | --- | --- | --- | --- |
| David R. Cook Roland R. Hall Autry, Hall & Cook, LLP 2100 East Exchange, Suite 2100 Tucker, Georgia 30084 cook@ahclaw.com hall@adclaw.com |  | D. Ronnie Lee President and CEO Walton Electric Membership Corporation P.O. Box 260 842 U.S. Hwy 78 NW drl9362@waltonemc.com |  |  |

So certified, this 26th day of August, 2019.

/s/ Curtis J. Romig

Curtis J. Romig