MOSSY BRANCH BATTERY FACILITY

PROJECT OVERVIEW

# EXECUTIVE SUMMARY

On July 29, 2019 the Georgia Public Service Commission (the “Commission”) issued a final Order Adopting Stipulation as Amended (the “Order”) under Dockets 42310 and 42311 in connection with Georgia Power Company’s 2019 Integrated Resource Plan (“2019 IRP”).  In accordance with that Order, and to evaluate the technical and economic performance of Battery Energy Storage Systems (“BESS”), Georgia Power Company (“Georgia Power” or the “Company”) has begun to develop 80 MW of BESS that will be self-owned and operated. The Company has chosen to develop and test three different configurations to maximize learnings. These configurations include large standalone transmission interconnected storage, solar plus storage, and small standalone distribution interconnected storage.

Consistent with the Order, Georgia Power submits this report to the Commission prior to undertaking construction and procurement of the project being proposed. This report includes the project plan for the large standalone transmission interconnected storage, hereinafter referred to as the Mossy Branch Battery Facility. As such, it provides the objectives, location, transmission evaluation, and detailed operating and testing plans for the project as required by the Order. The Company anticipates filing project plans for the solar plus storage and small standalone distribution interconnected storage configurations after all necessary project development has been completed.

# PROJECT OVERVIEW

The Mossy Branch Battery Facility will contain a 65 MWAC 4-hour BESS, providing a total energy of 260 MWh per cycle. This independently sited storage system, also referred to as standalone, will connect to and charge from the transmission grid. The Company has chosen to site this facility near an existing substation in Talbot County, GA, which is projected to provide optimum operational flexibility. The land used for construction and long-term operation of this facility is owned by Georgia Power, therefore no easements or leases are required for this project.

In addition to the efforts performed to identify an optimal site location, the Company has completed the necessary transmission studies for interconnection and executed the Large Generator Interconnection Agreement (“LGIA”) in March 2021. A copy of the LGIA has been provided with this report (“TS_Transmission_Evaluation.pdf”).

The Company has also carried out key development work related to the communication and control of the BESS. The Company anticipates the BESS primarily being controlled remotely and automatically by the Company’s Energy Management System (“EMS”) for responding to system events and for dispatching via the Automatic Generation Control (“AGC”) function. To fully maximize the value of storage, the Company will be upgrading the current AGC software to allow for optimized storage dispatching. When the BESS is not on AGC, the Company will have the capability to manually control the facility from a centralized operations, monitoring, and diagnostic center. More details on this subject has been provided in the attached Mossy Branch Battery Facility Operation and Test Strategy (“TS_Mossy_BESS_Operation&Test.pdf”).

# FINANCIAL ANALYSIS

Consistent with prior practice, the Company is providing the following financial analysis information:

- SAM Model. This spreadsheet provides total project costs and calculates the revenue requirement of the Mossy Branch Battery Facility.

“TS_SAM ('20)_6.0.1_MossyBranch.xlsm”

# PROJECT OBJECTIVES

The objectives of the Mossy Branch Battery Facility are to evaluate in a real-time environment the commercial operation performance of a standalone grid-charging storage asset and to refine the BESS operation and maintenance practices such that the asset’s useable lifetime is maximized. A detailed description of the testing strategy for these objectives has been provided in the attached Mossy Branch Battery Facility Operation and Test Strategy.

## Commercial Operation Performance

Unlike storage co-located with solar, a standalone system will be completely dependent on the electric grid for charging. As previously mentioned, the Company anticipates dispatching the facility remotely utilizing Automatic Generation Control (“AGC”), which currently schedules and dispatches other available generation resources. This facility will aid in validating daily and seasonal discharge schedules of standalone storage. Doing so, will allow operations to optimize the dispatch of these assets to enhance the system’s ability to meet demand.

The Mossy Branch Battery Facility will also support demonstrating the potential value streams this type of asset presents to the electric system. To demonstrate this, the Mossy Branch Battery Facility has been designed to perform the following use-cases at a minimum:

Operating Reserves (Spinning, Regulating, Contingency)

BESS, as a fast response unit, represents a new source of system flexibility. If called upon, the BESS can rapidly respond to changes in generation and demand faster than traditional generation. While the BESS is online and on AGC, any remaining energy capable of being discharged will be incorporated into the spinning, regulating, and contingency reserves calculations. This can release other resources to support other system needs.

Resource Adequacy / Capacity Value

Resource supply capacity defines the minimum amount of capacity required to meet the load under non-extreme operating conditions. BESS can be part of the resources that aid in meeting resource adequacy by committing the BESS to capacity during periods where it is deemed to have capacity value. This effectively translates into an operating constraint whereby the BESS could support other use-cases but would need to achieve a minimum State of Charge (“SOC”) by the beginning of the period where it has capacity value to support the resource supply capacity minimum requirements.

Generation Shifting / Energy Arbitrage / Energy Benefit

Utility scale BESS, unlike traditional generation resources, have the capability to flatten the effective system load shape. This is accomplished by charging and storing energy during periods of low demand then discharging energy to serve load during high demand periods. This shifting of energy allows the Company to maximize the utilization of renewable energy production and helps manage unit cycling to meet customer energy demands during peak periods.

Frequency Regulation / Automatic Generation Control

System frequency and inter-area flows are controlled by a combination of frequency droop control and AGC by dedicated generators. The balance between generation and load and the subsequent management of frequency is calculated via the area control error (“ACE”) equation. When system events occur that cause the ACE value to move outside the prescribed limits, generators controlled by AGC will be sent signals to maneuver and respond accordingly. By allowing the BESS to be placed on AGC control, the facility can use its sub-second response capability to respond to these excursions. Using the BESS to perform this role should decrease the time needed to bring the system back in balance, as compared to traditional generation resources.

Voltage Regulation / Reactive Power Support

Similar to other inverter-based generation, the BESS can provide power factor control by the inverter acting as a voltage source and operating in all four quadrants of the rated apparent power circle. This allows for the inverter to not only charge or discharge the battery, but to also supply or consume reactive power. This reactive power capability can be used to support the transmission system by either adjusting the BESS output reactive power in response to changes to the voltage at the point of interconnection or by following set-points from the transmission management system or the energy management system.

In addition to testing each use-case individually, the Mossy Branch Battery Facility will also be capable of value stacking, or also referred to as use-case stacking. Stacking these applications during operation will help the Company determine which use-cases are complementary to each other and how best to utilize the applications during different times of the day and throughout the year.

## Long Term Operation & Maintenance

The Company will develop key performance indicators for the Mossy Branch Battery Facility to inform and refine BESS operation and preventive maintenance practices. This will support maximizing the BESS’s value over its lifetime.

By analyzing the operational performance of the BESS relative to different factors, the Company can properly set future BESS operating constraints such that the Company can enhance the facility’s reliability and extend its useful life. Factors such as average cycles per day, state of charge, and temperature all have impacts on the battery’s degradation, and ultimately the available useable energy. Analyzing these factors in conjunction with the dispatch schedule will help optimize the commercial operation such that the BESS dispatch cost considers the impact to battery degradation.

The Company anticipates utilizing the support of the Engineering, Procurement, and Construction (“EPC”) Contractor for understanding the preventive maintenance and monitoring requirements to assure equipment reliability. While the Company has experience with inverter technology, utility scale battery storage requires different maintenance tasks and training. The Mossy Branch Battery Facility will help inform the Company’s maintenance program on items such as the necessary maintenance, labor, and spare parts for utility scale BESS, which will subsequently support providing efficient and effective maintenance for future storage facilities.

# ENGINEERING, PROCUREMENT, AND CONSTRUCTION

Through a competitive solicitation in accordance with the Order, the Company has selected an EPC Contractor to provide the EPC services for the Mossy Branch Battery Facility. The Company’s evaluation considered project costs, level of experience, technology performance, reliability, and safety. Once finalized, the EPC agreement will provide a turnkey, lump-sum agreement for construction of the BESS and auxiliary equipment, with terms similar to those of the Company’s other EPC agreements that have been executed in connection with recent self-build renewable projects. The agreement will require milestone payments by the Company only upon contractor achievement of specified construction milestones. Consistent with prior projects, the Company will  submit the EPC agreement to the Commission once finalized.

The Company will perform the transmission and interconnection work at the substation to deliver grid power at 115 kV to interconnect to the 34.5 kV Mossy Branch Battery Facility.

The Company anticipates work beginning in September 2021, with declaration of Commercial Operation expected in September 2023.