MOSSY BRANCH BATTERY FACILITY

OPERATION & TEST STRATEGY

Version 1.1

TABLE OF CONTENTS

1.	INTRODUCTION AND OBJECTIVES	3

Facility Description	4

Operational Framework	5

2.	TIMELINE	6

3.	BASELINE TESTING	7

System Performance Parameters	7

Roundtrip Efficiency Test Routine	7

Available Energy Capacity Test Routine	9

4.	BATTERY SYSTEM INTEGRATION	10

Interconnection	10

Communication & Control	10

5.	COMMERCIAL OPERATION PERFORMANCE	11

Voltage Regulation / Reactive Power Support	12

Resource Adequacy / Capacity Value	12

Generation Shifting, Frequency Regulation, and Operating Reserves	12

6.	LONG TERM OPERATION & MAINTENANCE	14

State of Charge Management	14

System Capacity Degradation	15

Auxiliary Power Consumption	17

Thermal Management System	18

Availability and Reliability	19

Preventative Maintenance	19

# INTRODUCTION AND OBJECTIVES

Georgia Power Company (“Georgia Power” or the “Company”) was granted authority as part of the 2019 Integrated Resource Plan (“IRP”) to develop, own, and operate battery energy storage system (“BESS”) demonstration projects for the purpose of evaluating the technical and economic performance of the system. The Company has chosen to develop and test three different configurations: large standalone transmission connected storage, solar plus storage, and small standalone distribution connected storage. The purpose of this document is to outline the operation and test strategy for the large standalone transmission connected BESS located at the Mossy Branch Battery Facility in Talbot County, Georgia.

Recent technical advancements and continuous cost reductions in battery technology make BESS a highly valued solution to address a wide range of challenges related to the generation and delivery of electric power across the grid. Utility-scale BESS, unlike traditional generation resources, have the capability to flatten the effective system load shape by acting as a load during low load periods (charging) and serving load during high load periods (discharging). These resources can also deliver additional benefits through other use cases such as providing system operating reserves, frequency response support, voltage regulation / reactive power support, and dispatch operational flexibility due to sub-second response capability. In order to fully optimize the operation of these assets, the Company has developed a strategy for testing and evaluating the Mossy Branch Battery Facility. The strategy is comprised of three areas of evaluation.

- BATTERY SYSTEM INTEGRATION

This facility will be the first independently sited BESS on the Company transmission system and will also be the first utility-scale BESS to be owned and operated by the Company. As with any new resource technology being connected to the system for the first time, there is a certain level of design validation needed to confirm safe and reliable integration with the electric power grid and reliable integration into the Company’s communication and control systems.

- COMMERCIAL OPERATION PERFORMANCE

Once the facility has achieved commercial operation, the Company will validate operation and performance capability in a real-time environment. The BESS will be able to perform several different use cases (also referred to as modes of operation), each creating their own value stream. By operating the facility in different modes of operation, including utilizing a priority based system to stack multiple modes, the Company will be able to assess the optimal strategy for dispatching future BESS resources to enhance the system’s ability to meet customer demand.

- LONG-TERM OPERATION & MAINTENANCE

In addition to optimizing the dispatch strategy, the Company also aims to optimize the maintenance and calendar lifetime of these assets. The current battery technology is subject to capacity degradation that can be attributed to multiple factors including calendar aging, number of cycles, and thermal management. During the test period the Company will obtain operational performance data to inform and refine BESS operation and preventive maintenance practices which in turn will support the Company’s objective of utilizing the full value of the BESS over its life.

## Facility Description

The Mossy Branch Battery Facility is a lithium-ion BESS interconnected to the 115 kV transmission bulk power system with an energy capacity of 260 MWh (65 MW / 4-hour). As seen in Figure 1, the BESS consists of three major sections:

Figure 1: BESS SIMPLIFIED DIAGRAM

- Battery Energy Storage: At its core, battery energy storage is comprised of battery cells formed in series to create a module. These modules are placed in series in racks, and multiple battery racks are then connected in parallel to form a single unit. Each unit is equipped with the following: a battery monitoring circuit for module level control, a thermal management system (“TMS”), and fire detection and suppression systems. The battery units are subsequently connected in parallel with other units to form a battery array. To increase system energy capacity to the desired level, multiple battery arrays are then connected in parallel.

- Power Conversion System: The Power Conversion System (“PCS”) will consist of inverters and associated power transformers. BESS utilize bi-directional inverters for direct current (“DC”) to alternating current (“AC”) power conversion during periods of discharge and then to rectify AC to DC power during periods of charging. A step-up transformer connected to the AC side of each inverter increases its output to medium voltage level. The energy then travels to a main power transformer, where the voltage is stepped up and subsequently transferred to the electric grid.

- Communication & Control System: An integral part of a BESS is its communication and control system. As shown in Figure 2, the BESS communication & control system  is driven by the site controller. This software system at the local facility level will collect, monitor, and control equipment operation data. The site controller will ensure that all battery arrays act in unison in accordance with the dispatch requirements provided from Fleet Operations. Operating data from the battery energy storage and power conversion system is transmitted to the site controller via the battery management system (“BMS”) and the inverter control, monitoring, and protection software. The BESS communication & control system will also interface with the Company transmission supervisory control and data acquisition (“SCADA”) system to ensure a real-time view into operations.

## Operational Framework

This section has been REDACTED in its entirety.

# TIMELINE

The total test period will last for a duration of three years after beginning commercial operation in September 2023. Baseline Testing will be performed semi-annually to document system parameters. The results of the testing will inform an Operation & Maintenance (“O&M”) analysis, which will review how certain operation and maintenance practices impact the reliability and lifetime of the asset. The Company will also perform an annual commercial performance analysis to review how the EMS operated the BESS and what value the BESS provided to the system. At the end of the test period, the Company will develop a final report that outlines the results of this project, including any lessons learned the Company anticipates on implementing for future storage assets supporting the electric system.

| Mossy Branch Evaluation Timeline | 2023 |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 |
| Integration Validation |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Baseline Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |
| O&M Analysis |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Commercial Performance Analysis |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Final Report |  |  |  |  |  |  |  |  |  |  |  |  |  |

# BASELINE TESTING

The purpose of this section is to outline a testing regiment to be used following commissioning services to capture key system performance parameters. The baseline testing will be performed semi-annually during the test period to document changes in system performance. Results from the baseline testing will support reviews of commercial operation performance as well as life cycle analyses. Detailed procedures describing roles and responsibilities, testing conditions, data collection steps, and data analysis will be developed once the BESS design has been completed.

## System Performance Parameters

The roundtrip efficiency (“RTE”) and available energy capacity are the key parameters to be established during baseline testing. These parameters will be determined by performing a daily charge/discharge cycle over a specified period. The baseline testing results will then be used to track the system degradation and performance over time.

In addition to available energy capacity and RTE, Table 1 outlines additional performance parameters that the Company will monitor throughout the test period. The charge duration, rated continuous power, and auxiliary load consumption share the same basic testing protocols as the available energy capacity test, therefore one set of tests can be performed to establish all the aforementioned parameter values. However, there is one exception for the Rated Continuous Power: the reactive power portion of the procedure will need separate testing to be performed in addition to the single test done for the active power aspect of the procedure.

Table 1: Test Procedure Duty Cycle

| System Parameter | Data Collection Requirements |
| --- | --- |
| Available Energy Capacity | SOC, MWh |
| Charge Duration | SOC, time |
| Rated Continuous Power | SOC, MW, time |
| Aux. Load Determination and Monitoring | SOC, MW, time |
| Roundtrip Efficiency | SOC, amp hours, MWh, time |

## Roundtrip Efficiency Test Routine

The Company plans to perform this test by cycling the BESS at various increments of rated discharge and charge power between the manufacturer’s recommended maximum and minimum state of charge (“SOC”) limits. If the rated discharge and rated charge power differ, then the lower of the power ratings will be used as the maximum rating for both discharge and charge so that they are symmetrical. By performing each cycle between the same maximum and minimum SOC values, approximately the same amount of DC amp hours will be transferred out of and into the energy storage medium at the same power rating for each cycle.

The data must then be normalized to determine the exact time required to transfer the same DC amp hours both for discharge and charge. Those times will be only slightly different for the discharge and charge but are large enough that they must be accounted for. The total energy transferred is then calculated at the storage medium, PCS, and point of interconnection (“POI”) with the transmission system during the periods associated with the equivalent duty cycle amp hours for discharge and charge. RTE values arrived at by transferring the same amount of DC amp hours are thus comparable at the equivalent discharge and charge power values ranging from rated discharge/charge to reduced power values of 75%, 50%, and 25% of rated discharge, and charge power are comparable based on the RTE results from each full duty cycle test for the selected ranges.

A maximum of one complete test cycle will be performed daily to allow for system stabilization and thermal equilibration. This test routine will require the BESS be operated in the same SOC range for six complete test cycles. The SOC test range will be the manufacturer’s recommended maximum allowable SOC and minimum allowable SOC.

Required Variables

Overall RTE will be measured using strategically placed meters. The Company anticipates these meters being located at the output of the BESS, at the transmission POI, and at a location to monitor auxiliary load.

The following variables will be required to calculate roundtrip efficiency:

- Accepted Charge Energy, (EC): This represents the energy accepted from the grid to the BESS during charging, excluding the energy required to satisfy separately metered auxiliary loads.

- Delivered Discharge Energy, (ED): This represents the energy delivered to the grid from the BESS during discharging, excluding the energy required to satisfy separately metered auxiliary loads.

- Consumed Battery Energy during Charge, (EBC): This represents the energy consumed by battery during charging.

- Consumed Battery Energy during Discharge, (EBD): This represents the energy consumed by battery during discharging

- Consumed Auxiliary Energy during Charge, (EAC): This represents the energy consumed to satisfy separately metered auxiliary loads during BESS charging.

- Consumed Auxiliary Energy during Discharge, (EAD): This represents the energy consumed to satisfy separately metered auxiliary loads during BESS discharging.

- Power Delivered During Discharge (PD): Power delivered by the BESS to the POI.

- Auxiliary Power Consumed During Discharge (PAD): Energy loss to parasitic loads internal to the system.

- Power Accepted During Charge (PC): Power accepted by the system during charge cycle.

- Power Consumed Auxiliary During Charge (PAC): Auxiliary power consumed by parasitic loads in the system during charge cycle.

RTE Equations

The AC roundtrip efficiency at the POI is determined by comparing the AC energy transferred from the BESS during the discharge cycle to the AC energy delivered to the BESS during the charge cycle to return the BESS back to the maximum SOC. The Company anticipates using the basic equations below for the RTE analysis:

ED=0x PD *td				Equation 1

EAD=0x PAD *td			Equation 2

Where x = time required to discharge equivalent dc amp hours to the grid and tD is the discharge time.

EC=0y PC *tc				Equation 3

EAC=0y PAC *tc				Equation 4

Where y = time required to charge equivalent dc amp hours from the grid and tC is the charge time.

RTE=100×ED-EADEC+EAC			Equation 5

## Available Energy Capacity Test Routine

This test will determine the stored available energy capacity of the battery storage. This evaluation will take into account the storage device, auxiliary loads, power conversion systems.

The Company plans to perform this test routine by cycling the BESS at various increments of rated charge and discharge while remaining within the maximum and minimum SOC limits. If the rated charge power and discharge power vary, then the lower of the two power ratings will used as the maximum rating for both the charge and discharge power. Available discharge/charge energy values are arrived at by transferring energy at various power values ranging from rated discharge/charge to reduced power values of 75%, 50% and 25% of rated discharge and charge power.

Required Variables

The following variables are required to determine BESS available energy capacity.

- Accepted Charge Energy, (EC)

- Delivered Discharge Energy, (ED)

- Consumed Auxiliary Energy during Charge, (EAC)

- Consumed Auxiliary Energy during Discharge, (EAD)

Available Energy Capacity Equations

The AC available energy is the energy that can be transferred from the BESS during a discharge cycle at the rated power output. Any energy that is transferred during discharge after the BESS power output drops 2% below the rated discharge power value will not be included in the capacity or available discharge energy at rated power calculations. The overall discharge/charge energy or capacity will be measured on the high side of the main power transformer.

Available Discharge Energy at Rated Power= ED-EAD	Equation 6

Available Charge Energy at Rated Power= EC-EAC		Equation 7

# BATTERY SYSTEM INTEGRATION

Like photovoltaic (“PV”) systems, BESS utilize inverter technology for power conversion between AC and DC power and also utilize transformers to increase or decrease voltage to the necessary levels. While this power delivery design is not new, the capability to both import and export energy for charging and discharging while also having the capability for sub-second dispatch response requires an additional level of analysis and integration validation. The two areas that have been identified as key components to integrating the BESS into the Company’s system is the facility transmission interconnection and the Company’s communication and control systems.

## Interconnection

All electric storage resources connecting to the bulk electric system, such as the Mossy Branch Battery Facility, will undergo performance validation testing during trial operations once the facility has reached normal, full-load operation. This performance validation testing must be satisfactorily completed prior to Southern Company Transmission approving the facility’s readiness for commercial operation under the Interconnection Agreement. A stand-alone BESS will require performance validation testing of applicable charging and discharging operational modes. The performance validation testing activities may include but are not limited to:

- Reactive Power Capability

  - The inverter-based storage unit will be required to demonstrate that it can produce and / or absorb within its full reactive capability to meet its voltage schedule or power factor requirement at the POI during both discharging as well as charging mode.

- Voltage Step Test

  - This test is conducted by changing the voltage set point and determining the transient response on the voltage and reactive power of the facility from before and after the step change, as well as after it reaches the new steady-state values.

- Frequency Step Test

  - This test is conducted by changing the frequency reference set point and evaluating the frequency response on the power output of the facility from before and after the step change, as well as after it has reached the new steady-state power output.

- Power Quality

  - Adherence to Southern Company Power Quality Policy which includes, but not limited to, harmonics and Rapid Voltage Change (“RVC”) testing.

## Communication & Control

The Mossy Branch Battery Facility will be utilized to test and validate the control and communication architecture developed for BESS. This architecture has been designed to support both local and remote operation of the site controller, battery system (including the TMS, BMS, fire protection/suppression, and safety systems), PCS, protection and control equipment, and balance of plant equipment. The BESS control system will help support the prioritization and transition between modes of operation and ensure that operating constraints are not violated to prevent any irreversible damage to the battery system.

As previously shown in Figure 2, control of the facility can be accomplished manually through the local operator workstation, manually through the remote OM&D Center, or automatically through the remote AGC system. The Company anticipates that the Mossy Branch Battery Facility will primarily be dispatched and controlled automatically by the AGC system and only moved to manual control during baseline testing or for maintenance purposes.

Testing of the communication and control architecture will occur as part of system commissioning and site acceptance testing to be performed by the Engineering, Procurement, and Construction (“EPC”) Contractor. With respect to communication and controls, the testing will allow for evaluation of the following:

- Validate communication protocols that support data exchange thru the various site equipment and that such equipment operates as intended, including point lists validation and alarming confirmation.

- Validate that the physical infrastructure supporting remote communication of historical and operational data from the local site controller to the OM&D Center and AGC system accurately transmits data without lag to facilitate a fast response time to system events.

- Validate proper function of the Human Machine Interface (“HMI”) which will provide visual control capabilities for the site and remote operator, as well as support alarming and maintenance functions.

- Validate the integration and accurate operation of site’s protection and control and metering systems with the site controller.

- Validate the site controller settings associated with functions listed in the Commercial Operation Performance section. This will ensure the correct implementation and operation of the various use cases control logic programmed in the site controller.

- Validate the site controller settings associated with operating constraints such as maximum and minimum state of charge, maximum and minimum cell charge voltage, minimum battery string charge current limit, maximum and minimum cell temperature, and state of health.

- Validate AGC operation via confirmation of signals from fleet, as well as confirmation that the site responds in an acceptable timeframe.

# COMMERCIAL OPERATION PERFORMANCE

Once operational, the Mossy Branch Battery Facility will be capable of performing the following use cases: voltage regulation / reactive power support, resource adequacy, generation shifting, frequency regulation / AGC, and reserves. The BESS will perform one or more of these operations at a time depending on the needs of the electric system. As previously stated, the Company anticipates using the EMS and AGC function to operate the BESS. The Company will allow this system to dictate the mode of operation.

The BESS will be evaluated based on its ability to perform the various operational services. The purpose of this demonstration asset is to not only understand whether or not the asset can perform the various services, but also to identify which of these services provide the most value to the Company and its customers. Therefore, the operation of the Mossy Branch Battery Facility will be evaluated annually over the test period to determine the services that are providing the most value to the system. The Company will utilize internal and external resources to perform these post operational analyses to better inform the Company’s future resource planning decisions.

## Voltage Regulation / Reactive Power Support

Utility-scale BESS can effectively compensate for the power fluctuations resulting from the increasing renewable energy grid connections. This is accomplished by the BESS rapidly injecting or absorbing active and reactive power. Other inverter-based generation, such as PV generation, also have this capability. The difference is that a BESS can provide voltage support essentially around the clock, whereas PV only has this capability for the portion of the day when the facility is generating energy.

When it is identified that the transmission system requires voltage support, the EMS will send the appropriate signals indicating a needed response.  This mode of operation will be tested initially as part of the transmission performance validation testing during trial operations. Thereafter, the Company, as part of its annual evaluation, will analyze how often the BESS was called upon to support this function, response times, and the overall impact to system reliability.

## Resource Adequacy / Capacity Value

Resource supply capacity defines the minimum amount of capacity required to meet the load under non-extreme operating conditions. BESS can be part of the resources that aid in meeting resource adequacy by committing the BESS to capacity during periods where it is deemed to have capacity value. This particular use case is not necessarily a specific mode of operation, but rather a strategy for meeting current commitments and demand. Due to this, the Company does not anticipate any specific testing or operation to validate this use case. Instead, the resource adequacy benefits provided by the Mossy Branch Battery Facility will be considered as part of the broader commercial operation evaluation.

## Generation Shifting, Frequency Regulation, and Operating Reserves

The use cases of generation shifting, frequency regulation, and reserves will be dictated by Fleet Operations and the Company’s EMS. Fleet Operations at Southern Company is responsible for reliably and economically committing generation to meet the system’s load demand. This process involves three major areas:

- Unit Commitment

  - Committing units on a rolling ten-day window, meeting demand reliably and economically.

- Real-Time Operations

  - Modifying commitment intra-day to better reflect system changes while meeting demand reliably and economically.

- AGC

  - An algorithm within the EMS system that dispatches units in real-time to meet system needs reliably and economically.

Fleet Operations will fully integrate the Mossy Branch Battery Facility into its commitment and dispatch process described above. This will allow the BESS to operate and successfully demonstrate the applicable use cases. Fleet Operations will operate the battery as a resource to meet system demand needs, including using the resource for reliability needs as well as being used to lower system production cost. After BESS operations, analysis of the Real-Time dispatch can be evaluated and examined to show example timeframes of the above use cases.

Below summarizes the use cases that will be utilized by Fleet Operations as part of the commitment and dispatch process.

- Generation Shifting / Energy Arbitrage / Energy Benefit

  - Fleet operations through its commitment/dispatch process will attempt to arbitrage the BESS when possible. A typical commitment schedule will look to charge in times of low-energy prices and discharge in times of high energy prices. This arbitrage could be manually scheduled or automated through AGC. In most instances due to the BESS quick response time, the BESS will remain on AGC, allowing for real-time arbitrage.

- Area Control Error (“ACE”) / Frequency Regulation

  - Primary Frequency Response: This response will be dictated at the site level and will be handled by the local site controller.

  - ACE: With the BESS remaining on AGC it will be available to respond to ACE excursions.  These excursions can be caused by numerous events, but when they occur the system needs to respond quickly. By allowing the BESS to be placed on AGC control, the BESS can rapidly respond to these system frequency and ACE events ultimately bringing these parameters back within their prescribed limits much faster than a traditional thermal generation resource.

- Operating Reserves

  - Spinning: While the BESS is online, any remaining discharge energy will be incorporated into the spinning reserves calculation.

  - Regulation: While the BESS is online and on AGC, any remaining discharge energy will be incorporated into the regulation reserve calculation.

  - Contingency: While the BESS is online, any remaining discharge energy will be included in the contingency reserve calculation.

- Use Case Stacking:

  - By fully integrating the BESS into the commitment/dispatch process, the BESS will be able to stack multiple use cases and operate based on the current system need. As Fleet Operations commits the system for reliability and production cost, the BESS will be a new flexible resource used to meet these goals. Whether the BESS is being used to meet energy needs or meet reserve needs, it will be optimized within the fleet to reduce total production cost.

# LONG TERM OPERATION & MAINTENANCE

Much like other generation facilities owned and operated by Georgia Power, the Company will aim to optimize the maintenance and calendar lifetime of these assets. During the test period, the Company will track key operational performance indicators to inform and refine BESS operation and preventive maintenance practices. These parameters include:

- State of Charge Management

- System Capacity Degradation

- Auxiliary Power Consumption

- Availability and Reliability

- Thermal Management System

- Preventative Maintenance Practices

The Company will capture the necessary system performance values to evaluate the above parameters via the periodic baseline testing, as well as through the normal operation data being logged by the local site controller. This data will be transmitted to the OM&D Center, where mechanisms will be established to monitor normal operations, identify any system deviations, support diagnosing any system issues, and tracking key performance indicators required to support this test plan. The Company anticipates reviewing and analyzing the information quarterly to determine if any operational parameters need changing.

## State of Charge Management

It is generally accepted that a mid-range state-of-charge (“SOC”) promotes long battery life with less capacity degradation. In consideration of this, the Company will aim to keep the average SOC at or below 60% and above 20% SOC, especially during any periods of prolonged rest. If the battery manufacturer for the Mossy Branch Battery Facility imposes any additional SOC restrictions as a condition of the long-term capacity guarantee, then those constraints will also be incorporated into the operating goals.

Another objective will be to evaluate the impact of using different use cases on the SOC management. Some use cases, such as spinning reserves, will place a value on having the batteries at or near 100% SOC to pick up load if another generating asset trips off. To properly manage the average SOC requirements, BESS operation in high-SOC use cases will need to be balanced by another use case that lowers battery capacity to 0% SOC. This will help to avoid extended operation at high SOC and promote an average SOC in the mid-range.

Evaluation of SOC Management with respect to BESS operation will allow the Company to better understand:

- The accuracy of the SOC estimated by the BMS.

- The factors that go into successful SOC management.

- The factors that run contrary to successful SOC management.

Timeline & Test Strategy

The BESS SOC value is transmitted by the local site controller to the OM&D Center at regular intervals during normal operation. The average SOC will be tracked continuously as two performance variables. The 7-day average SOC will be calculated as a rolling average and will not be reset. The 90-day SOC will be calculated each calendar quarter and reset at the end of each quarter. Reasons or causes of excursions outside of the target SOC range will be noted for better understanding of the challenges to controlling it.

Data will be analyzed for each quarter and for each use case tested. Average SOC analysis will be coordinated with BESS performance testing when validating each operating mode. The Company will utilize this data to check and adjust operational parameters to achieve optimal SOC management. Additionally, the accuracy of the SOC estimated by the BMS will be checked during annual performance tests.

## System Capacity Degradation

The energy capacity of a BESS is a primary design and operating parameter. The energy capacity (in MWh) determines how long (in hours) a BESS can deliver rated power (in MW). The Mossy Branch Battery Facility is designed to discharge for four hours at 65MW output, which requires 260MWh of energy capacity. In practice, it takes longer than four hours to recharge because the system is only about 85% efficient.

The battery capacity is expected to degrade with calendar aging and energy throughput. Degradation curves are predicted by the battery manufacturer based on individual cell test results. Extra energy capacity is initially installed, and capacity augmentation is planned over time to offset the expected capacity degradation and maintain the 260MWh design energy capacity.

The Company anticipates procuring long term performance guarantees, which include a capacity guarantee. BESS suppliers guarantee that actual system degradation will be better than or equal to a set of degradation curves, otherwise the supplier will correct the issue. An example of such degradation curves can be seen in Figure 3 below, where the vertical Y-axis is the guaranteed remaining capacity and the horizontal X-axis is the calendar life since commercial operation. The number of cycles per day is the (total cumulative MWh discharged ÷ 260) / (calendar days since commercial operation). Energy capacity is initially demonstrated during the Site Acceptance Testing and by annual performance tests thereafter. Energy capacity can also be estimated whenever the BESS is fully discharged during normal operation

Degradation occurs so gradually and is influenced by so many variables that the Company does not expect to answer questions about how each of those variables affect the degradation rate. Instead, the Company’s evaluation will help:

- Determine an accurate method between annual performance tests for measuring energy capacity utilizing data for daily operations.

- Analyze actual degradation rate versus the battery manufacturer’s predicted degradation curves.

- Determine an approach for forecasting when and if battery augmentation is necessary to maintain the original BESS capacity for a specified period of time.

REDACTED

Figure 3 – EXAMPLE FAMILY OF DEGRADATION CURVES

Timeline & Test Strategy

The first demonstration of the Mossy Branch Battery Facility energy capacity will occur during the Site Acceptance Testing performed by the EPC Contractor as part of the turn-key EPC Agreement. Annual performance tests will be fostered each year by the EPC Contractor to determine if the BESS has met or exceeded the predicted degradation.

The BESS capacity can also be demonstrated informally any time the BESS is fully discharged from 100% SOC to 0% SOC. The discharge rate is measured and recorded and can be integrated over time to yield the total energy discharged. The Company anticipates utilizing the OM&D Center to track energy charged and discharged from the BESS which will facilitate estimating the remaining capacity during operation. Additionally, the Company may also choose to perform an informal capacity estimate if there are significant changes in the operation of the BESS or whenever the BESS is called upon to respond to major system events.

The Company believes that three years of operation should enable a clear degradation pattern to emerge from annual test results. If any augmentation occurs to the system, the guaranteed degradation curves will require updating. This is accomplished by adding the new augmented capacity with its own predicted degradation to the existing capacity in its degraded state.

## Auxiliary Power Consumption

Auxiliary power is the parasitic load associated with a BESS, the energy that is consumed but not stored or discharged. It contributes to the losses that reduce round-trip efficiency. Thermal management is typically the biggest consumer of auxiliary power. Other components include the BMS, BESS control system, fire protection system, lighting, and other auxiliary systems.

Auxiliary power consumption is one of the larger BESS operating costs and is guaranteed by the supplier not to exceed a given value. The guaranteed value varies depending on how much heat is generated by cycling the batteries and by the external heating due to the outdoor ambient temperature. Example curves of an auxiliary power consumption guarantee can be found in Figure 4.

For safe battery operation, auxiliary power should be supplied from multiple sources to ensure it can reliably support the BESS. One source of auxiliary power will include a transformer to derive it from the transmission POI. The Company also intends on including other auxiliary power sources such as a metered industrial account from the local distribution system and a portable generator connection for use during construction, maintenance outages, and grid outages.

The Company plans on performing the following with respect to auxiliary power consumption:

- Track auxiliary power demand and energy consumption (from any source) monthly.

- Compare the auxiliary power consumption with guaranteed consumption over time.

- Track the cost of auxiliary power with respect to BESS production savings.

- Determine which Company commercial rate plan minimizes the BESS operating cost.

  - Can BESS operations be tailored to take advantage of a TOU or Demand rate?

  - Does the BESS impose a significant load on the distribution system?

- Decide whether to normally take auxiliary power from distribution or transmission.

Timeline & Test Strategy

A baseline performance test of auxiliary power consumption will be performed as part of the site acceptance tests. Energy consumption and power demand will be tracked continuously to predict anticipated electric charges. Data will be analyzed quarterly or when there is a significant change in the BESS use case.

Data gathering over time can be used to correlate auxiliary power consumption with use cases based on the energy throughput (number of daily cycles), the depth of discharge, and the power at which the BESS charges and discharges. Slow charging during off-peak hours will reduce the parasitic heat load.  Auxiliary power consumption and ambient temperature can be noted on days when the batteries rest to correlate auxiliary power consumption with ambient temperature independently of the use case.

Auxiliary power demand and energy consumption data points will be monitored by the local site controller and the OM&D Center, as well as logged in the data historian. The energy and demand charges for varying rates can be modeled to estimate monthly electric charges.

REDACTED

Figure 4 – EXAMPLE AUXILIARY POWER GUARANTEE CURVES

## Thermal Management System

The BESS will have a Thermal Management System (“TMS”) which is responsible for keeping the batteries in a set range of temperatures. If the battery temperature falls under a minimum limit or above a maximum limit, the TMS will provide support to bring the battery temperature back within the required range. During charging and discharging of batteries, a significant amount of heat can be generated, and this heat must be managed properly to ensure the long-term health of the system. Operating the batteries outside of its thermal parameters will directly affect the long-term health of the batteries. The Company will evaluate the following as part of this test plan:

- Understand the impact of TMS failures.

- Determine best maintenance practices for maintaining the TMS.

- Optimize operations to limit strain on the TMS.

- Analyze the effectiveness of the TMS design.

Timeline and Test Strategy

The TMS will continually be monitored by the OM&D Center and any availability issues will be captured using the Company’s reporting processes. During operation, the TMS performance will be monitored and compared to BESS state of health. Battery degradation is directly tied to TMS performance, and this will be evaluated on an annual basis.

## Availability and Reliability

The Mossy Branch Battery Facility will be designed and built with utility-grade equipment and systems to facilitate a high level of reliability. Reliability must be demonstrated on a continuing basis and fostered by an operation and maintenance plan tailored to the system components. As part of long term performance guarantees, BESS suppliers typically guarantee a 98% availability of the facility. However, such long term performance guarantees come at a cost. The Company plans to utilize this facility to better understand the maintenance practices necessary to achieve 98% availability in a BESS. The objectives with respect to availability and reliability include:

- Capture all events or failures that cause derates or unplanned outages, including identifying any common failure modes.

- Develop O&M and/or capital budgets based on observed equipment failures and reliability.

- Update spare part list as needed for optimal spare parts inventory.

- Quantify what economic value availability provides, or what cost is incurred for de-rates or unavailability in $/MWh.

Timeline & Test Strategy

The Company will utilize the OM&D Center to track reliability of the major subsystems including batteries, BMS, inverter / PCS, and the TMS. Any other critical system components that cause unavailability will be added to the list there after. All events will be documented and evaluated by applying Company root cause analysis processes. Results will be utilized to provide updates to the Company’s preventive maintenance practices, BESS O&M budget projections, and required site spare parts list.

## Preventative Maintenance

The BESS and its supporting components require certain Preventative Maintenance (“PM”) plans which are important to the ability for this equipment to run for an extended period. For the Mossy Branch Battey Facility, the initial PM plans will be developed by and, to an extent, supported by the EPC Contractor. Most PMs to be performed are driven by warranty requirements, with a majority consisting of only inspections. A periodic evaluation of the PMs will allow for a determination of the necessary spare parts and replacement items needed on site to maintain reliability. Capturing this data over several years will assist in creating proper material cost for yearly budgeting. Additionally, The Company will utilize this facility to confirm actual hours needed to complete required maintenance as compared to supplier recommendations. This information will be used to develop labor hour estimates for future BESS facilities.

With the Mossy Branch Battery Facility, the Company aims to perform the following:

- Develop the necessary skillsets to self-perform maintenance on BESS.

- Determine needed replacement items and cost and develop associated budgets

- Determine the actual labor hours required to maintain the BESS facility.

- Develop standard Operating and Maintenance labor budgets for BESS.

Timeline and Test Strategy

In order for the Company to develop the proper skills to maintain and operate BESS, the Company anticipates having the EPC Contractor provide support during commercial operation. Company maintenance technicians will utilize the opportunity learn and observe best practices with respect to BESS. Additionally, Company technicians will also provide regular independent inspections of equipment and the general facility to ensure continued integrity and functionality. Both the EPC Contractor and the Company’s OM&D Center will monitor equipment remotely in efforts to identify any potential equipment issues early.

The cost of material and labor used during PMs will be captured to inform the Company’s maintenance strategies. The Company will utilize enterprise tools to capture this data for evaluation and review annually for any required updates.

# glossary of terms

AC		Alternating Current

ACE		Area Control Error

AGC		Automatic Generation Control

BESS		Battery Energy Storage System

BMS		Battery Management System

DC		Direct Current

DER		Distributed Energy Resource

EMS		Energy Management System

EPC		Engineering, Procurement, and Construction

HMI		Human Machine Interface

MW		Megawatt

MWh		Megawatt-hour

O&M		Operation & Maintenance

OM&D		Operation, Monitoring, & Diagnostic Center

PCS		Power Conversion System

PM		Preventative Maintenance

POI		Point of Interconnection

PV		Photovoltaic

RTE		Round Trip Efficiency

RVC		Rapid Voltage Change

SCADA		Supervisory Control and Data Acquisition

SOC		State of Charge

TMS		Thermal Management System