BEFORE THE PUBLIC SERVICE COMMISSION

STATE OF GEORGIA

SAWNEE ELECTRIC MEMBERSHIP 	)

CORPORATION,	)

)

Petitioner,	)

)

v.	)		Docket No. 43899

)

GEORGIA POWER COMPANY	)

)

Respondent.	)

# PRE-FILED DIRECT TESTIMONY OF

HAROLD V. GRESHAM

September 9, 2021

# PRE-FILED DIRECT TESTIMONY OF

# Harold v. gresham

# ON BEHALF OF GEORGIA POWER COMPANY

# GPSC DOCKET  No. 43899

Q.	PLEASE STATE YOUR NAME, TITLE AND BUSINESS ADDRESS.

A.	My name is Harold (Hal) V. Gresham. I am employed as the Interconnection Planning Supervisor for Georgia Power Company (“Georgia Power” or the “Company”), located at 241 Ralph McGill Boulevard, Atlanta, Georgia 30308.

Q. 	PLEASE STATE YOUR RESPONSIBILITIES AS INTERCONNECTION PLANNING SUPERVISOR.

A.	As the Interconnection Planning Supervisor, I manage a team responsible for delivering interconnection requests from renewable and distributed energy resources to Georgia Power Distribution and Transmission. I am also responsible for leading the strategic deployment of generation sources, including analysis of solar, battery storage, electric vehicles, biomass, and microgrids on the system.

Q.	PLEASE SUMMARIZE YOUR EDUCATION AND PROFESSIONAL EXPERIENCE.

A.	I graduated from the Georgia Institute of Technology with a Bachelor of Electrical Engineering. I have worked for the Company since I was in college when I participated in Georgia Tech’s Cooperative Education program with Georgia Power. Through 2001, I worked for Georgia Power and Savannah Electric Power Company in various engineering roles of increasing authority. From 2002 through 2008, I served as the Engineering Supervisor in several regional positions managing engineering teams, assisting Area Distribution managers, and managing the implementation and oversight of major distribution projects in Gainesville, Alpharetta, and Marietta. I served as the Assistant to the General Manager of Distribution, Engineering, Construction, and Maintenance in 2008 and was promoted to Distribution Safety and Health Supervisor in 2009.  From 2011 to 2014, I managed the Gwinnett area Distribution for construction, engineering, and operations as the Distribution Operations Manager. From 2014 through 2017, I served as the Centralized Engineering Services Manager and managed a team of engineers designing and managing projects for the Georgia Department of Transportation, city, and county relocation projects. In 2017, I transitioned to the role of Distribution Planning Supervisor where I managed and directed the planning studies and solutions development for the Georgia Power distribution system for almost four years. In 2020, I moved to my current role as Interconnection Planning Supervisor.

Q.	WHAT IS THE PURPOSE OF YOUR TESTIMONY?

A.	My testimony provides the technical and factual basis for the Georgia Public Service Commission (“Commission”) to confirm that Georgia Power is lawfully providing retail electric service to the new, single-metered premises located at Johns Creek Town Center, 3630 Peachtree Parkway, Suwanee, Georgia 30024 (the “Premises”). The Premises, which consists of an electric vehicle (“EV”) charging array, had a connected load at initial full operation greater than 900 kW. Therefore, the Premises qualifies for customer choice pursuant to the large load exception under the Georgia Territorial Electric Service Act (“Territorial Act”), O.C.G.A. § 46-3-8(a)(5).

Q.	PLEASE DESCRIBE THE PREMISES.

A.	The Premises consists of an EV charging array, made up of six power cabinets served by Georgia Power that are connected to four EV charging dispensers. Two of the charging dispensers are 175 kW in size (labeled as 150 kW) and two are 350 kW in size. The charging dispensers are powered by the six power cabinets located on the adjacent equipment pad. Each of the 150 kW dispensers are connected to one power cabinet, whereas each of the 350 kW dispensers are connected to two power cabinets. All six of the power cabinets have the same capacity. Specifically, each power cabinet has an AC-rated input of 190 kW and a DC-rated output of 175 kW, resulting in a total AC connected load of 1,140 kW. The Premises is located in the parking lot of the Johns Creek Town Center shopping mall, which is in unincorporated Forsyth County in Sawnee EMC’s assigned territory for electric service.

Q.	IS THE PREMISES NEW?

A.	Yes, the Premises is newly constructed. The Premises was added to the existing parking lot of the Johns Creek Town Center shopping mall and began receiving electric service in April of 2021.

Q.	HOW IS THE PREMISES IS METERED?

A.	The Premises is single-metered.

Q.	PLEASE DESCRIBE GEORGIA POWER’S SERVICE TO THE PREMISES.

A.	Georgia Power serves the Premises through a 750kVA transformer that is connected to a 25kV distribution line that already serves other customers in the Johns Creek Town Center shopping mall. A 750kVA transformer is capable of serving more than 750 kW of load and is sufficient to serve the Premises. Georgia Power installed the 750kVA transformer based on the estimated connected load for the Premises at initial full operation.

Q.	WHAT IS THE AMOUNT OF CONNECTED LOAD GEORGIA POWER IS SERVING AT THE PREMISES?

A.	Georgia Power is serving 1,140 kW of connected load at the Premises. This is determined by the nameplate input rating of each of the six power cabinets, which is 190 kW per cabinet.

Q.	IN YOUR OPINION AND EXPERIENCE, IS THE NAMEPLATE CAPACITY THE APPROPRIATE METRIC TO USE TO DETERMINE HOW MUCH LOAD THE COMPANY’S FACILITIES MUST BE DESIGNED TO SERVE?

A.	Yes. When the customer requests electric service, the customer self-identifies and shares with Georgia Power how much load it will require for its operations. Georgia Power then uses this information to prepare to serve the customer’s premises. Typically, the information shared is the nameplate capacity of the primary equipment being served. To design and install a system based on anything less than the connected load based on the equipment nameplates would risk impairment of service to the customer and others in that area of distribution, equipment damage, and potential public safety concerns in the event the connected load came fully online.

Q.	WILL THE INSTANTANEOUS DEMAND FOR THIS CHARGER TYPICALLY BE 1,140 kW?

A.	Most likely not.

Q.	IS IT APPROPRIATE FOR GEORGIA POWER TO DESIGN SERVICE BASED ON THE TYPICAL INSTANTANEOUS DEMAND?

A.	No, it’s not. To provide safe, adequate, and reliable service, Georgia Power must design its service based on the connected load, not the typical demand. Service design and construction based on an estimate of the maximum instantaneous demand would only be an estimate and would risk damage to the power system and customer equipment, outages, and safety risks.

Q.	DOES GEORGIA POWER SERVE OTHER EV CHARGING ARRAYS?

A.	Yes.

Q.	IS GEORGIA POWER’S APPROACH TO DETERMINING HOW TO SERVE THE PREMISES CONSISTENT WITH HOW IT SERVES OTHER EV CHARGING ARRAYS?

A.	Yes. Georgia Power designs service to EV charging arrays based on connected load, not typical demand levels.

Q. 	DOES THIS CONCLUDE YOUR TESTIMONY?

A.         Yes.