Bin 10230,

241 Ralph McGill Boulevard, NE

Atlanta, GA  30308-3374

November 10, 2021

The Honorable Tricia Pridemore, Chair

Georgia Public Service Commission

244 Washington Street, SW

Atlanta, GA  30334-5701

RE:	Georgia Power Company QF Cost Study Report; Docket No. 4822

Dear Madame Chair:

Georgia Power Company (“Georgia Power”) submits this report to the Georgia Public Service Commission (“Commission”) pursuant to your request to provide the interconnection and delivery study results and costs associated with three proposed qualifying facility (“QF”) projects, each of which intends to sell 100% of their electric output to Georgia Power pursuant to the Public Utility Regulatory Policies Act of 1978 (“PURPA”). These three state-jurisdictional QF projects are known as Stagecoach (IC-882), Five Bridges (IC-883) and Alligator Creek (IC-894). All three QFs have completed the interconnection study process and have negotiated QF standard offer contracts (“PPAs”) with Georgia Power that are proceeding towards execution and Commission approval. These PPAs will include the interconnection and delivery costs outlined in this report.

Background

The Commission’s March 11, 2021 Final Order in Docket No. 4822 (the “Final Order”) required Georgia Power to develop and publish state-jurisdictional QF Interconnection Procedures (see Ordering Paragraphs J and K). Because these three QFs entered the interconnection study process prior to approval of these procedures, they used the available Large Generator Interconnection Procedures (“LGIP”). Because the LGIP does not include a full delivery study, Georgia Power then conducted separate delivery (a/k/a “designation”) studies to ensure each QF’s output can be firmly delivered to Georgia Power customers in compliance with PURPA. All studies were performed by Southern Company Services, Inc. (“SCS”).

For ease of review, Attachment A provides a summary of the interconnection-related and delivery-related network upgrades and estimated costs that are included in the individual reports. Each QF was the subject of two studies and received two study reports, which are provided as Attachments B through G. These Facilities Study Reports detail the necessary improvements for the QF to physically interconnect to the transmission system. SCS then issued the QF Designation Study Reports (the “Delivery Study Reports”), which detail the improvements necessary for firm energy delivery from the QF to serve system load. These reports estimate the network upgrade costs that, pursuant to the Commission Staff’s stated interpretation of the Final Order, are to be funded by the QF and then refunded by Georgia Power’s customers after each QF achieves commercial operation.

The Final Order states:

“The Commission finds and concludes that it is appropriate that QFs shall continue to pay their total reasonable interconnection costs and that modifications to the transmission system (Network Upgrade Costs), that are required in order to facilitate the QF’s interconnection shall be refunded (100%) back to the QF.” The Commission finds that [it] is appropriate to refund the Network Upgrade Costs back to the QF since these upgrades benefit the transmission system and therefore benefits all customers with improved grid reliability.” (Final Order at 9; See also Ordering Para B.).

With respect to a QF, there are two types of Network Upgrades identified in the reports – those to facilitate a QF’s interconnection, and those to facilitate transmission/delivery of the QF’s output. Specifically, the additions, modifications, and upgrades to the Georgia Power electric system required at or beyond the point of interconnection to accommodate the interconnection of the QF (the “Interconnection-related Network Upgrades”) are captured in the Facilities Study Reports found in Attachments B through D. The additions, modifications, and upgrades to Georgia Power’s electric system or to an affected system required for the firm delivery of the QF’s output to Georgia Power’s native load customers in compliance with PURPA (“Delivery-related Network Upgrades”) are captured in the Delivery Study Reports provided in Attachments E through G.

For purposes of comparison and information, Georgia Power has researched several similarly situated, non-RTO states and is not aware of any other utility that refunds network upgrades to QFs. PURPA requires customer indifference, which means that interconnection of the QF and purchase of the QF’s output should not increase costs to customers. Refunding these Network Upgrades to the QF will eliminate almost all incentive for a QF to site in a location that minimizes interconnection and delivery costs for customers. For reference, one may contrast the cost-effectiveness and siting efficiency between the Commission-approved requests for proposals (“RFPs”), planned through the integrated resource planning (“IRP”) process and managed under the Commission Rules, with PURPA’s requirement to purchase all QF output whenever offered from the QF’s selected location. Georgia Power’s RFPs offer customers renewable energy and renewable energy credits (RECs) bundled at prices well below projected avoided cost, whereas the PURPA program allows the QF to retain the RECs and requires customers to pay actual avoided cost. An RFP selects winning projects with the lowest overall costs to customers, including interconnection and delivery costs, which promotes logical generation siting and efficient transmission system expansion, whereas a QF may site its project without regard to how the location impacts customer costs. Additionally, the Commission controls the pace and the amount of renewable energy procured on behalf of customers through the IRP/RFP process, whereas the PURPA program requires customers to purchase all the energy the QF desires to deliver. Finally, renewable generators in the RFP process are obligated through long term agreements to provide renewable energy at known prices to customers, whereas PURPA PPAs offer no certainty that the renewable energy will ever be delivered for use by customers.

Interconnection Facilities Study Reports Generally

The purpose of an Interconnection Facilities Study Report is to evaluate the impact of a proposed generator’s interconnection on the safety and reliability of Southern Companies’ transmission system, based on information gathered through the study and using standard criteria and assumptions. The Facilities Study Report outlines the estimated Interconnection-related Network Upgrades needed to facilitate interconnection. For these three QF projects, these upgrades and cost estimates can be found collectively in Attachment A, or in Table e.3.b “Southern Companies Interconnection Upgrades – Beyond the POI” in each individual QF’s Facilities Study Report found as Attachments B through D.

The Interconnection Facilities Study Report has two components: an interconnection evaluation and a delivery screen. The interconnection evaluation identifies the Interconnection-related Network Upgrades required for the proposed interconnection configuration. The delivery screen evaluates the potential capability of the local area transmission system to receive the generator’s output. Interconnection-related Network Upgrades may be identified if the delivery screen determines the local area transmission system is incapable of accommodating the generator’s full requested output. The delivery screen does not establish a delivery queue position nor constitute an offer of transmission service. As such, it does not replace the need for a QF to undergo a separate Delivery Study. PURPA requires firm transmission of output to help ensure no impermissible curtailment of the QF’s output, and the Delivery Study, not the delivery screen, identifies the necessary Delivery-related Network Upgrades to ensure Georgia Power can receive the QF’s output firmly in compliance with PURPA.

Delivery Study Reports Generally

The purpose of a Delivery Study Report is to identify any Delivery-related Network Upgrades needed to maintain safety and reliability, and to ensure firm delivery of the QF’s output to customers. The Delivery Study Report identifies constraints in the existing local area transmission facilities (see Table 1 in Attachments F and G) and then outlines the estimated Delivery-related Network Upgrades needed for the firm delivery of the QF’s power to Georgia Power’s native load customers in compliance with NERC reliability standards and PURPA. Construction of the Delivery-related Network Upgrades helps to ensure no impermissible curtailment of the QF will occur in violation of PURPA. The Delivery Study Report also includes the estimated timing for construction of the needed Delivery-related Network Upgrades. As mentioned below in reference to Five Bridges and Alligator Creek, in some cases, particularly when the Delivery-related Network Upgrade is not already included in the ten-year transmission plan, there can be construction timing challenges presented by the project. For these three QFs, these upgrades and estimates can be found in Attachment A, or in Table 2 “Transmission Solutions for Attributable Designation Constraints” in the Delivery Study Reports found in Attachments F and G.

Network Upgrade Costs Identified for the Stagecoach QF Project (IC-882)

The Facilities Study Report for IC-882 identified necessary Interconnection-related Network Upgrades to interconnect the Stagecoach QF project to the transmission system equal to an estimated $5,150,000. These costs are solely related to interconnection of this QF and require Georgia Power to construct a new 115 kV interconnection substation and modify or upgrade five additional 115 kV substations (e.g., update relay settings and anti-islanding transfer trip equipment).

The final Delivery Study Report for IC-882 identified no additional costs to deliver the QF’s 80 MW on the transmission system. Georgia Power notes that the Delivery Study results for this Stagecoach project initially estimated $17,480,000 for necessary Delivery-related Network Upgrades caused by the presence of this QF in its self-selected location. These costs were related to the need to upgrade 18.4 miles of existing 115 kV transmission line to allow firm delivery of the QF’s output. As part of the delivery study process, Georgia Power contacted Georgia Transmission Corporation (“GTC”) to ask about the status of a project that was ahead of Stagecoach in the delivery queue. GTC indicated it would voluntarily “step aside” to allow Georgia Power’s QF project to go ahead of GTC’s prior-queued delivery service reservation. As a result, these Delivery-related Network Upgrades are no longer needed and therefore, the Stagecoach Delivery Study Report (Attachment E) reflects no Delivery-related Network Upgrade costs.

Network Upgrade Costs Identified for the Five Bridges QF Project (IC-883)

The Facilities Study Report for IC-883 identified necessary Interconnection-related Network Upgrades to interconnect the Five Bridges QF project to the transmission system equal to an estimated $5,085,000. These costs are solely related to the interconnection of this QF, whose selected location will cause Georgia Power to construct a new 115 kV interconnection substation and will require the modification or upgrading of two additional 115 kV substations.

The Delivery Study Report for IC-883 identified transmission projects required to deliver the 80MW from the Five Bridges QF project on the transmission system equal to an estimated $37,910,000. This includes reconductoring or rebuilding approximately 47.8 miles of four existing 115 kV transmission lines, which in the case of the Arlington Primary line, is estimated to be complete by June 1, 2027. Constructing in challenging terrain, such as in low-lying areas with poor soil conditions, adds to the complexity and cost. For example, the 11.2 miles of the Blakely Primary to Webb 115kV transmission line to be rebuilt for this project crosses the Chattahoochee River and so presents challenging terrain and requires more permitting and detailed construction plans. Georgia Power further notes that the rebuilding of 9.6 miles of the George Dam – Abbeville 115kV transmission line and 10.5 miles of the Blakely Primary – Webb 115kV transmission line will cost an estimated $14,110,000, and these improvements are located in the state of Alabama.

Network Upgrade Costs Identified for the Alligator Creek QF Project (IC-894)

The Facilities Study Report for IC-894 identified necessary Interconnection-related Network Upgrades to interconnect the Alligator Creek QF project to the transmission system equal to an estimated $5,205,000. These costs are solely related to interconnection of this QF, whose selected location will cause Georgia Power to construct a new 115 kV interconnecting substation and modify an existing substation to, among other things, update relay settings and install anti-islanding protection. Constructing this new substation also requires Georgia Power to modify an existing 115 kV transmission line to interconnect the substation. Also identified in the Facilities Study Report for IC-894 is an estimated $600,000 in additional cost for contingent facilities that will be caused by the Alligator Creek QF project if an identified GTC project is not completed (see Attachment D, Table e.4.a – Southern Companies Interconnection Upgrades).

The Delivery Study Report for IC-894 identified transmission projects needed to deliver the 80 MW from the Alligator Creek QF on the transmission system equal to an estimated $30,500,000. This includes rebuilding 27.7 miles of the Eastman Primary – Vidalia 115 transmission line to ensure firm delivery of the QF’s output in compliance with PURPA. The project completion date is currently estimated to be June 1, 2026.

Conclusion

Georgia Power submits these interconnection and delivery study cost reports for the QF projects known as Stagecoach (IC-882), Five Bridges (IC-883) and Alligator Creek (IC-894) as requested by the Commission. If you have any questions or need additional information, please call me at 404-506-3044.

Sincerely,

/s/ Kelley M. Balkcom

Kelley M. Balkcom

Director of Regulatory Affairs

Attachments

For the Commission’s information, none of the interconnection- or delivery-related upgrades identified in these studies are included in Georgia Power’s current ten-year transmission expansion plan, which means these projects are to be constructed solely to interconnect and take firm delivery from these QFs in compliance with PURPA.

Georgia Power notes that under the newly proposed state-jurisdictional QF Interconnection Procedures, state-jurisdictional QFs (those selling output only to Georgia Power pursuant to PURPA) will proceed through one integrated and concise study process that will identify all necessary network upgrades and network upgrade costs at one time, in one report. The new procedures contemplate one comprehensive study process that includes both interconnection and delivery components to be included in the QFIA.

The Stagecoach and Five Bridges Facilities Study Reports are labeled “Re-Study” Reports because both requested increases in the MW output from 72 MW to 80 MW, which was considered a material modification under the LGIP. A Re-study was conducted to evaluate the additional capacity, which resulted in the Facilities Re-Study Reports for IC-882 and IC-883 included as Attachments B and C.

E.g., GTC, MEAG, Alabama Power, Gulf Power.

Under the newly proposed state jurisdictional QF Interconnection Procedures, a separate delivery study will only be necessary if a QF has a FERC-jurisdictional interconnection and must proceed through the LGIP to obtain a FERC-jurisdictional interconnection agreement. In such case, the costs of the Delivery-related Network Upgrades would be identified and included in the negotiated QF Standard Offer Contract in compliance with the Final Order. (See Stipulation at 10).

As of the date of this report, the Delivery Study Report for IC-883 is in draft form while Georgia Power awaits additional information from an affected system.

As of the date of this report, the Delivery Study Report for IC-894 remains in draft form while Georgia Power finalizes the construction schedule.