HR-1-1

Information requested by: Georgia Interfaith Power & Light – Sherrier (Tr. 63)

Question:

Q	During Winter Storm Elliott, 244 megawatts of Georgia Power's CTs were unavailable during Christmas Eve morning. Does that sound right?

A	(Witness Grubb) Subject to check.  I don't have those.  I know we've provided some information in the hearing requests.  I don't have them with me.

…

Q	And about over half of the Georgia Power capacity resour- -- Georgia Power-owned capacity resources that were unavailable during that time were combined cycle units?

A	(Witness Grubb) Subject to check.

Q	That -- the number I have in front of me is 1102 megawatts.

…

Q	Well, you -- I think you just answered this question.  But for the CTs and the CCs that were unavailable, was that gas unavailability or equipment failures?

A	(Witness Grubb) I can't recall if it was a gas availability or a unit availability issue.

MR. SHERRIER:  Well, can I make that a hearing request, Mr. Chairman?

CHAIRMAN SHAW:  Yes, sir.

MR. SHERRIER:  Identify the units that were unavailable during the highest reliability risk event.

…

CHAIRMAN SHAW:  So restate your question for your request.

MR. SHERRIER:  We'd like the company to identify the units that were unavailable during that critical time frame and the reason for that unavailability.

Response:

See the table below identifying the units with unavailability events and associated reasons for the unavailability events during the period of highest reliability risk during Winter Storm Elliott in December 2022. This information is provided for Georgia Power-owned capacity resources for the same time period included in Hearing Request 1-5 Supplemental from the direct hearings and Hearing Request 2-1 from the rebuttal hearings for the 2023 IRP Update proceeding in Docket No. 55378.

This information is not provided for Georgia Power’s aggregated capacity power purchase agreement (“PPA”) resources due to confidentiality provisions in the contract terms with PPA counterparties.

Winter Storm Elliott (Events during period of December 24, 2022, Hours 1-13 CST)

|  | Unavailable Capacity (MW) | Reason for Unavailability Event |
| --- | --- | --- |
| GPC-Owned Capacity Resources | 2,061 |  |
| Combined Cycles Total | 1,102 |  |
| McDonough Unit 4 | 808 | Unit-related issue: Frozen valves caused unit trips |
| McIntosh Unit 11 | 294 | Unit-related issue: Valve issue caused unit trip |
| Combustion Turbines Total | 244 |  |
| McDonough CT 3B | 40 | Dual fuel unit; Moisture frozen in fuel filter for ultra-low sulfur diesel; non-firm natural gas unavailable from market for this unit during this unavailability event. |
| McIntosh CT 2 | 94 | Unit-related issue: Cooling system issue |
| McManus CT 4B | 55 | Unit-related issue: Fuel filter pressure issue |
| McManus CT 4F | 55 | Unit-related issue: Generator breaker issue |
| Coal Steam Total | 644 |  |
| Scherer 3 | 644 | Unit-related issue: Transmitter failure due to freezing caused unit trip, also experienced fan issue |
| Nuclear Total | 71 |  |
| Hatch Unit 2 | 71 | Planned unit derate |

Notably, no outage events for Georgia Power-owned capacity resources during this time period were related to lack of fuel availability or deliverability.