## Sheet1
Bowen ELG ZLD O&M Cost
High Estimated Total O&M Costs with Encapsulation (with Gypsum) | 750 GPM | REDACTED | Flow based of 750gpm/24/7/365 discharge and encapsulation with Gypsum.
Additional Assumptions
1. Chemical usage, ash quantities, and personnel have the potential to be optimized.Example- Baghouse ash can be used and potentially grindind the bottom ash and using it.
2. Calculations based off 85% volume reduction. Additional capital equipment could achieve further volume reduction
3. The clarifier sludge has a great potential to replace the encapsulation lime reducing cost.
4. Estimates removed the EPRI assumption of selling fly ash and then buying it back
5. Removed lost fly ash sales
6. Solids disposal costs not included
7. Membrane replacements are capital.
8. Electricity and evaporator heating not included
Fly ash cost, purchased, $/ton | REDACTED
Quick lime cost, $/lb. | REDACTED
Gypsum Sales Lost, $/ton | REDACTED
Lost fly ash sales, $/ton | REDACTED
Baghouse ash Produced, tons/yr. | 47500
Bowen, fly ash produced, tons/yr. | 320000
Bowen, fly ash available for solidification, tons/yr. | 320000
Bowen, Chloride Bleed, gpm | 750
Bowen, RO reject flow req. solidification, gpm (85% Recovery) | 112.5
Reject Flow, tons/yr. (10.8 lb./gal density) | 319302
Total Required Fly Ash, ton/yr. (Encapsulation: 35% FA, 35% Brine, 25% Gypsum, 5% QL) -EPRI Formula | 319302
Total Required Gypsum, ton/yr. | 228072.8571
Total Required Quick Lime for Purchase, tons/yr. | 45614.5714
Total Fly Ash Required for Purchase, tons/yr. | 0
Purchased Fly ash cost/yr. | REDACTED
Lost Gypsum Sales cost/yr. | REDACTED
Lime cost/yr. (Encapsulation) | REDACTED
Total Solids for Disposal, tons/yr. | 684218.5714
Total O&M Costs for Solidification, using peak Purge flow rate | REDACTED
Lost Fly Ash Sale | REDACTED
Capital Maintenance Items (Membrane Replacement, etc) | REDACTED
Chemicals/Consumables | Pounds per Day | Estimated $ per Pound | Total
Hydrated Lime or Soda Ash (Phys/Chem) | 45146.02 | REDACTED | REDACTED
HCl /Sulfuric | 3084.3 | REDACTED | REDACTED
Centrifuge Polymer | 110 | REDACTED | REDACTED
Maintenance Consumables -(oil, grease, probes, etc.) |  | REDACTED | REDACTED
Sodium Hydroxide - Evaporator | 16652 | REDACTED | REDACTED
Anti-Scalant- Magnesium | 300 | REDACTED | REDACTED
Anti-Scalant - Calcium/Sulfate | 300 | REDACTED | REDACTED
Anti-foam | 111.6 | REDACTED | REDACTED
Variable O&M Total- 750 GPM |  |  | REDACTED
Additional Personnel (12) |  |  | REDACTED | REDACTED