STF-JKA-1-9

Question:

For a number of years, the Company has taken steps to mitigate risks of cold weather reliability. Please describe all efforts undertaken since the 2022 IRP including capital investment and O&M expense, and explain how those steps have paid off, and how the Company’s Aurora and SERVM modeling assumptions have been revised since the 2022 IRP as a result of the mitigation efforts undertaken.

Response:

Since the 2022 IRP, cold weather outage assumptions in the model have been adjusted to account for the ongoing winterization improvements performed across the System. In the 2021 Reserve Margin Study, incremental cold weather-related outages for all modeled resources were anticipated to start when system-weighted temperatures fell below 13°F. In the 2024 Reserve Margin Study, this threshold was adjusted downward to 10°F but only for retail resources owned and operated by Southern Company. For contracted resources, the threshold was increased to 18°F due to fewer winterization improvements being performed on these units. In addition to the threshold, a geographic adjustment was also made at each generation site to account for differences between local temperature and the system-weighted temperature. Part I, Section I of the 2024 Reserve Margin Study provided in Technical Appendix Volume 1 details the cold weather outage modeling methodology and assumptions applied. The Aurora modeling for the Resource Mix Study applies the target reserve margin determined in the Reserve Margin Study to help identify an optimized resource expansion plan. Loads modeled in the Resource Mix Study are based on normal weather, so no incremental extreme weather outages are applied.

Southern Company is currently implementing a fleetwide winterization program with the goal of not only improving the reliability of freeze protection systems at each plant but also lowering the minimum operating temperature and freeze related parameters. This includes adding/replacing various components such as heat tracing, insulation, instrument enclosures, heated tube bundles, equipment enclosures, and other auxiliaries related to protecting components during cold weather events. Procedures have also been updated to assure compliance with NERC EOP-012-2 Extreme Cold Weather Preparedness. To date, Georgia Power has invested over $100M capital and over $7M O&M in this effort. As a result, the Georgia Power fleet winter reliability continues to improve. No unplanned generation weather related events were experienced for Company owned resources during Winter Storms Enzo and Cora.