STF-JKA-2-12

Question:

Refer to Technical Appendix Volume 1, “2025 GPC ECS.docx” page 4 related to MATS RTR compliance and associated stack testing and monitoring equipment cost.

    - Describe the current status of procuring and installing continues emissions monitoring (CEM) equipment.

    - Provide a projected project timeline describing approvals, engineering, procurement, installation, testing, and final compliance.

Response:

- Currently, there are two Particulate Matter (“PM”) Continuous Emissions Monitoring Systems (“CEMS”) that have been temporarily installed at Plant Bowen and Plant Scherer. These are portable systems, designed to be moved to each of the seven coal-fired steam generating units within the Georgia Power fleet to test the systems to ensure they meet the compliance requirements.

The Company is currently working to procure the CEMS equipment in 2025.

- The Company plans to procure the CEMS in the third quarter of 2025. Installations are expected to occur in the first and second quarters of 2026. Initial certifications are scheduled to start in the third quarter of 2026 and should be completed by the end of 2026.

The Company is in the process of completing testing with the temporary monitors, site preparation work for permanent installation, and working on procurement and contracting to complete the certifications for the PM CEMS systems to comply with the compliance date of July 8, 2027.