STF-JKA-2-18

Question:

Refer to “2025IRP_AV_BowenU1-4_TRADE SECRET.xlsx” tab: “Study.”  Please explain the “capacity equalizer” assumptions provided in column I.  Describe any station service or derate assumptions and provide workpapers supporting the assumptions.

Response:

The “capacity equalizer” assumption defined on the “Study” tab is meant to account for capacity differences among environmental compliance pathways. The Effluent Limitations Guidelines (“ELG”) “No Cessation” Pathway would require the plant to install a zero liquid discharge (“ZLD”) system to treat scrubber wastewater. It is assumed that this would add a station service load of approximately 10 MW for the entirety of Plant Bowen. The co-fire pathway would require the same ZLD system and therefore the same approximately10 MW of incremental station service load. The 100% gas conversion pathways assume a net capacity increase of approximately 20 MW for Plant Bowen Units 1-2 and a net capacity increase approximately 30 MW for Plant Bowen Units 3-4. This assumption accounts for the reduction in station service load related to the removal of fuel handling equipment and environmental equipment such as the scrubber. The carbon capture and sequestration (“CCS”) pathway assumes a 25% derate due to a large station service load and process steam requirements associated with the carbon capture facility.