STF-JKA-2-20

Question:

Refer to the Company’s assumptions for Gaston 1-4,A as described in Table 1 of the Unit Retirement Study, and footnote 3 which states: “The Company did not complete a study evaluating the extension of Gaston 1-4 beyond 2035 given the age of the units.”

    - Please explain if there is any technical limitation to the continued operation of the Gaston units beyond 2035 based on age.

    - Please explain if environmental controls would be required at Gaston to comply with ELG rules if operating beyond 2035.

    - Please explain if environmental controls would be required at Gaston to comply with EPA 111 rules if operating beyond 2035.

    - Please explain if environmental controls would be required at Gaston to comply with MATS rules if operating beyond 2035.

Response:

        - There are no technical limitations to the continued operation of the Gaston units beyond 2035 based on age.

        - There are no additional environmental controls required for Gastons Units 1-4 or A to comply with the Effluent Limitations Guidelines (“ELG”) Rule beyond 2035. The only environmental control required to be installed at Gaston Units 1-4 to comply with the ELG Rule is piping and pumps needed to achieve a closed-loop Remote Submerged Chain Conveyor system to meet the Zero Liquid Discharge requirement for Bottom Ash Transport Water. This project is currently underway and will be complete by end of 2025.

        - Additional environmental controls are not expected for Gaston Units 1-4 to comply with the 111(d) regulation. While the final requirements are subject to U.S. Environmental Protection Agency approval of the State Plan developed by the Alabama Department of Environmental Management, these four units currently utilize natural gas as the primary fuel. The Company expects natural gas would be part of the compliance strategy for these units. Gaston Unit A is not currently subject to the 111 GHG Rules.

        - Additional environmental controls would not be required for Gaston Units 1-4 to comply with Mercury and Air Toxics Standards (“MATS”). MATS is not applicable to Gaston Units 1-4 or A because these units meet the definition of a “natural gas-fired electric utility steam generating unit” in the regulation.