STF-JKA-2-21

Question:

Refer to Technical Appendix Volume 1, “2025 IRP McIntosh Upgrades TRADE SECRET.docx” which states, “The scope of this upgrade includes replacing rotating blades and stationary vanes in the CTs (two CTs per combined cycle), combustor replacement, increasing firing temperature and shaft limits, and additional operating mode flexibility.”

        - Has GPC solicited cost proposals for these upgrades? Provide the contract and/or scope and price term sheet documents supported the estimated costs and increase in capacity (summer and winter) used in the economic analysis.

        - Provide all supporting documents pertaining to the forecasted capital cost estimate and the forecasted O&M estimates.  Please include details related to contracting including but not limited to any Long Term Service Agreements with contractors or capital budgets for the remaining life of the units.

        - Is the Company aware of any other units in the U.S. that have already implemented the same scope of upgrades?  Please provide all relevant peer documentation on the proposed upgrades.

        - Provide all supporting documents related to the required FT cost and fuel availability assumptions relied on in the economic analysis.  How did the Company determine the cost of the additional firm transportation and availability? Please explain.

        - Please provide documentation from General Electric explaining the benefits of the upgrades, and discussing General Electric's experience upgrading other similar units.

        - Please provide examples of other units where General Electric has performed similar upgrades and state when the upgrades were performed.

Response:

- Georgia Power has received a budgetary proposal and expected performance estimates from GE Vernova for the proposed combustion turbine (“CT”) upgrades at the McIntosh combined cycle (“CC”) units. The performance data provided by GE Vernova includes information for the current CT (identified as 7F.04 ECP4 HOR0 in the upper left hand corner) and for the proposed CT upgrade (identified as 7FA.05 Tech Pkg). Please see STF-JKA-2-21 Attachment A TRADE SECRET.

- Please refer to STF-JKA-2-21 Attachment B TRADE SECRET and STF-JKA-2-21  Attachment C TRADE SECRET for the cost estimate for the upgrade in 2024 dollars.  The commercial terms for the upgrade with GE Vernova, which are anticipated to be incorporated into a Contract Amendment to the existing Long Term Service Agreement (“LTSA”), have not been finalized. REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED.

- REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED. The proposed McIntosh CC upgrade is tailored to Georgia Power’s need so we cannot confirm that the scope is identical. The Company does not have peer utility unit related documents related to the proposed upgrade.

- The analysis assumes a total of 30,000 MMBtu per day of additional firm transportation (“FT”) required for the upgrades on McIntosh Units 10&11. The cost included in Technical Appendix Volume 1 is representative of a rate composed from two separate FT contracts: (1) 10,000 MMBtu per day of existing FT capacity priced at Southern Natural Gas (“SNG”) FERC gas tariff as found on SNG’s website, and (2) 20,000 MMBtu per day from a planned expansion on REDACTED REDACTED, for which there is an executed Precedent Agreement and for which information is provided in JKA-1-13 Attachment TRADE SECRET with a note regarding upgrades on slide 15.

- STF-JKA-2-21 Attachment D TRADE SECRET identifies some of the benefits for upgrading from a 7FA.04 CT technology to a 7FA.05 CT technology. Please note that the upgrade proposed for the McIntosh CC also includes winter capacity enhancements such as cold day power augmentation and cold day peak firing. As noted in the response to subpart (c), we have no documentation from GE related to its experience for the specific upgrade proposed for the McIntosh CC. REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED.

- Please these the Company’s response to subpart (c) concerning information for other units where similar upgrades have been performed.