STF-JKA-2-23

Question:

Refer to Technical Appendix Volume 1, “2025 IRP Nuclear Upgrades TRADE SECRET.docx”

        - What licensing and NRC approvals will be required for the nuclear upgrades?

        - What is the timeline and checkpoints needed to get all appropriate approvals?  Provide a list of all activities expected and the estimated time for each activity to be completed.

Response:

- The Nuclear Regulatory Commission (“NRC”) regulates the maximum power level at which a commercial nuclear power plant may operate. This power level is used, with other data, in many of the licensing analyses that demonstrate the safety of the plant. This power level is included in the license and technical specifications for the plant to operate within. NRC controls any change to a license or technical specification, and the licensee may only change these documents after NRC approves the licensee's application for change. The process of increasing the maximum power level at which a commercial nuclear power plant may operate is called a power uprate. The licensee submits a formal License Amendment Request (“LAR”) to obtain approval.

- The traditional timeline for NRC review and approval for a power uprate is 18 months.  The licensee conducts the engineering analysis oversight of the appropriate Original Equipment Manufacturer (“OEM”) of the nuclear reactor technology to ensure the appropriate technical basis to support the power uprate. The engineering analysis is approximately a 2-year process to ensure the appropriate calculations and modification scope is certified to be correct prior to NRC submittal for review and approval.

Vogtle 1&2 uprate timeline:

  - Preliminary Engineering	February 2025 - January 2026

  - Fuel transition LAR development	January 2026 – January 2027

  - Fuel transition LAR NRC review and approval	July 2027 – January 2029

  - Power Uprate LAR development	April 2026 – June 2028

  - Power Uprate LAR NRC review and approval	February 2029 – July 2030

These schedules are projections at this point and will be finalized in the 3rd quarter of 2025.

Hatch uprate timeline:

- Combined power uprate/MELLA+ LAR preparation	July 2025 – March 2027

- LAR final preparation 	April 2027 – June 2027

- Power uprate/MELLA+ NRC review and approval	July 2027 – December 2028

These schedules are projections at this point and will be finalized in the 3rd quarter of 2025.