STF-JKA-2-31

Question:

Refer to Technical Appendix Vol 2, “2025 IRP Technology Screening TRADE SECRET.docx” See Attachment B: Technology Application Standards (“TAS”) Data Summaries on page 20 describing the estimated REDACTED run hours and REDACTED starts per year for Simple Cycle CT with SCR.  See also Footnote 10 which states, “10. The presence of SCR allows for advanced class (H and J) gas turbines to meet NOx emission requirements; because these advanced class gas turbines with SCR and CO catalyst have a lower upfront capex and a lower heat rate than F- or G-class simple cycle CTs with SCR and CO catalyst, these serve as the basis for generic CT with Future Controls instead of F- or G-class CTs.” Please explain if the Companies modeled NOx requirements or CT capacity factor limits for new CTs in the Aurora Resource Mix Study.  If so, please reconcile the requirement in Aurora to this statement.

Response:

In the Aurora modeling for the Resource Mix Study, the Company applied a 20% capacity factor limit to all combustion turbines (“CTs”), both new and existing, in aggregate. This capacity factor limit is not based on a specific environmental rule or requirement but is intended to broadly represent limitations on combustion turbine operation that could be attributed to permit limitations and performance standards under the Clean Air Act. The new generic CTs modeled are also subject to NOX emission allowance fees. The run hours and starts per year for CTs with Selective Catalytic Reduction (“SCR”) provided in Technical Appendix Volume 2, 2025 IRP Technology Screening TRADE SECRET Attachment B represent the typical expected operation of a generic CT and are assumed for purposes of developing cost and performance metrics for generic CTs.