STF-JKA-2-35

Question:

Refer to Technical Appendix Volume 2 “2025 IRP Resource Mix Study TRADE SECRET.docx” Section 3.3.1 Demand Side Options, which states, “Dispatchable DSOs were included as capacity resources in this study. Each interruptible contract load was appropriately adjusted to equate it to the supply side by one or more of the following corresponding factors: availability factor, loss factor, and Effective Load Carrying Capability (“ELCC”).”  See also “Georgia Power and System DSO Data - 2025 IRP TRADE SECRET.xlsx” rows 31:33 on the Dispatchable DSO tabs.

        - Provide a narrative explanation regarding the derivation of the ELCC assumed for each program and the supporting study, historical performance, and/or relevant documentation relied on to make such an assumption.

        - Provide a narrative explanation regarding the derivation of the Demand Comparison Factor assumed for each program and the supporting study, historical performance, and/or relevant documentation relied on to make such an assumption.

        - Provide a narrative explanation regarding the derivation of the Loss Expansion Factor assumed for each program and the supporting study, historical performance, and/or relevant documentation relied on to make such an assumption.

Response:

- Each of the six active demand side option (“DSO”) programs was independently simulated with the SERVM reliability model. The table below details the variables and restrictions applied to each program based on program parameters. The Georgia Power Demand Plus Energy Credit (“DPEC”) program is modeled with a unique load shape based on actual customer energy usage. The addition of this load shape in the modeling process more closely aligns available interruptible energy with modeled reliability events as opposed to assuming contracted capacity is available in all hours. The response magnitude applied to the DPEC program is based on the historical performance from the last three interruption events that occurred on January 7, 2014, October 10, 2017, and December 24, 2022.

| Programs | Days Per Week Dispatch Limit | Hours Per Day Dispatch Limit | Hours Per Year Dispatch Limit | Response Magnitude |  | Restrictions |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Winter | Summer |  |
| GPC DPEC | 7 | 8 | 100 | 65% | 65% | Customer Load Shape |
| GPC RTPeDA | 7 | 24 | 8760 | 100% | 100% | 24-hour customer notify |
| GPC RTPeHA | 7 | 24 | 8760 | 100% | 100% |  |
| GPC CVR Level 1 | 7 | 24 | 8760 | 100% | 100% |  |
| GPC CVR Level 2 | 7 | 24 | 8760 | 100% | 100% |  |
| GPC Temp Check (Winter) | 5 | 4 | 40 | 100% | 100% | 5 events allowed per season |
| GPC Temp Check (Summer) | 5 | 5 | 50 | 100% | 100% | 5 events allowed per season |

There were two steps performed to determine the final DSO effective load carrying capability (“ELCC”) values. Step 1 consisted of evaluating each DSO program independently as the first-in program in a system that had no other DSO programs embedded. These “first-in” values tend to be the highest possible ELCC values but do not consider the synergistic or antagonistic interactions of multiple DSO programs, each with their own unique parameters. Step 2 consists of evaluating the entire DSO fleet in aggregate. This is performed by adding all DSO resources at the same time and evaluating them together to determine a single ELCC value, representing the entire DSO fleet. The final step consists of individually weighting each DSO program based upon their relative program size and first-in ELCC value while ensuring that the final ELCC capacity MW values of all programs sum up to the aggregate, fleet-wide ELCC value determined in step 2. This aggregate step ensures that the reliability contribution of the entire DSO fleet is not over or understated. See STF-JKA-2-35 Attachment A for the program ELCC calculations and the DPEC program load shapes that were applied.

- The Demand Comparison Factor is not applicable to Georgia Power’s programs and is set to 100% for all programs. It is not a consideration in the calculation.

- The Loss Expansion Factor provides an adjustment to the capacity value to account for the fact that load reduced at the customer meter results in greater avoided capacity at the generator level because of losses on the system in the delivery of energy. The values are calculated as part of a load flow study and are based on the level of service taken by the majority of customers enrolled in the respective program or rate. See STF-JKA-2-35 Attachment B.