Per Commission Rule 515-7-5-.07, the EDC shall include the following minimum filing requirements in its Annual USF Facilities Expansion Plan filing:

|  | - A detailed written technical description of the project(s). The technical description will include, but not be limited to, a discussion of the type, size, and length of the proposed facilities and the proposed route and the community and/or company that will be served. The technical description will affirmatively state if a proposed approach main line-extension is new main or an extension or expansion of existing main as defined in 515-7-5-.01(j)(k). There will be a discussion of the type and size of main proposed to be replaced. The technical description will affirmatively state if the EDC is or is not certificated to serve in the counties where the facilities will be constructed. |
| --- | --- |

Emanuel County

This project proposes to serve a wood pellet manufacturing plant in Emanuel County near the town of Nunez, Georgia south of Swainsboro.  The plant is expanding, including installing natural gas equipment to dry the material used to make wood pellets.  This expansion is expected to employ as many as 12 additional people.

AGL currently operates a 12”/6” pipeline originating in Alamo at the Alamo tap station.  The pipeline originates at the Alamo tap station and traverses northeast along AGL and public right-of-way, feeding areas in Wheeler, Toombs, Treutlen, and Montgomery Counties.  AGL has determined that an additional segment of this pipeline must be upsized to serve this project.  AGL has obtained approval to upsize segments of this pipeline upstream of this proposal, specifically completing 8,300 feet of 12” approved by PSC in the 2019 USF Annual Plan, 12,012 feet of 12” in the 2022 USF Annual Plan, and 19,455 feet of 12” in the 2023 USF Annual Plan.  Further, in the recent past economic development and legislative entities have also expressed a desire to procure additional gas supply capability on the AGL system to serve this project and potentially enhance the ability to attract commercial and industrial growth to this area.

AGL proposes to upsize an additional segment of the existing 6” steel pipeline with 12” steel to serve this project.  The proposal is to install approximately 28,000 feet of 12” steel (MAOP 300 psi) along AGL right-of-way, continuing from the end of the Alamo Segment 3 project which was completed in 2025 adding 19,455 feet of 12” steel, and approximately 18,000 feet of 6” steel (MAOP 300 psi) along SR 56, Trout Trail, and Grande Creek Road.  In addition, the proposal includes an approximately 1,400 foot 4” steel service (MAOP 300 psi) to address this need.

Please see MFR-4 Maps of Proposed Corridors Wheeler.  AGL is certificated to serve this area.