Emanuel County Project

STF-17-1	MFR 1: Please address the following in a revised filing:

    - Who is the customer wanting as service?

    - What Pool Group will the customer reside?

    - Is this a new customer or a current customer?

    - Is this a new facility?

    - Is this new gas load or does the customer have current gas service?

    - Are there any constraints in the Pool Group in serving this customer?

    - If the project is approved, are there any foreseeable constraints to the Pool Group once the new customer begins operations?

    - Today, who is the gas marketer serving the customer?

RESPONSE

Inasmuch as AGL (a) included information required by Rule 515-7-5-.07 in its current filing, and (b) provided additional information requested by this STF-17-1, a revised filing is not necessary.  The Company provides the following responses:

- The customer requesting service is LJR Forest Products.  Please see the as-filed MFR-5.  MFR-5 labels the customer as IJR Forest Products in error, but the correct entity is LJR Forest Products.

- This customer is located in the Brunswick pool.

- This is a proposed new customer.  Please see the as-filed MFR-1.

- No, but the facility does not currently have gas service.  The customer is expanding the plant to include natural gas equipment. Please see the as-filed MFR-1.

- See response to STF-17-1iv.

- There are no current constraints in the Brunswick pool that would prohibit service to this customer except that construction of facilities as proposed in the as-filed MFR-4 are required to serve.

- Future proposals to expand natural gas infrastructure in this area will be dependent on requested loads and locations of future firm customers.  AGL evaluates service requests on a case-by-case basis.  It is possible that an existing interruptible customer on this system may request to switch to firm service upon completion of this project.  This situation, if it occurs, does not constitute a constraint, but AGL may be required to propose further facilities expansion to enable this ID/FD switch.

- See response to STF-17-1v.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-2	Regarding the engineering of the project please answer the following:

        - What is the timeline for construction to begin and end? When will the service be turned on?

        - Regarding the 6 inch steel upgrade to 12 inch steel, what is distance in feet and miles from where Alamo Phase 3 that ends at South 2nd Street south of Glenwood to Ailey Lothair Rd northeast of Mt. Vernon?

        - By upgrading the 28,000 feet of 6 inch steel to 12 inch steel, what will be the increased capacity (load) of the intrastate transmission line from Alamo to Mt. Vernon

        - There is an existing 6 inch main that runs southwest of Swainsboro along SR 56 ending at Trout Road. This  project calls for a new extension along Trout Rd to the new customer.

It is approximately 31.7 miles from where the 12-inch steel intrastate transmission line proposed upgrade will end north of Mt. Vernon. See Map-1 below.

With the proposed route of the new extension to the customer, it is approximately 3.8 miles. See Map-2.

How can the transmission line 12 inch steel upgrade ending at Mt. Vernon help provide natural gas capacity and service to the new customer when there is no connection between the transmission line and the current 6 inch steel main ending at SR 56 and Trout Road? Would any pressure increases needed to serve the customer have to originate in the Swainsboro area?

        - Does AGL agree that the 6 inch extension along from SR 56 to Trout Road to Grande Creek Road to Old Nunez Road will provide sufficient capacity to serve the new customer without the need for the Glenwood to Mt. Vernon transmission line upgrade?

        - Does this project have an impact on AGL 2025 – 2027 Capacity Supply Plan?

        - Since AGL has proposed continuing the transmission line upgrade for an additional 28,000 feet, what are the direct benefits to areas east of Mr. Vernon with this additional capacity since it appears to have no connection in providing increase capacity in the Swainsboro region?

RESPONSE

- If the project is approved AGL will develop a detailed construction schedule at that time and can inform Staff of the preliminary timeline.  Subject to development of a detailed construction schedule, AGL preliminarily estimates that the project could take as long as 24 months to complete.  Service will be turned on when construction activities are complete such that natural gas can be safely provided to the customer’s equipment.

- The straight-line distance between the two stated points is approximately 26,700 feet (5 miles).

- Hydraulic modeling indicates that the 12” pipe could enable incremental supply in excess of 800,000 MCFH to the system inclusive of the 75 MCFH requested by the customer depending on future customer load and location.  Each future potential customer will be evaluated on a case-by-case basis to determine potential system improvements.

- Gas to all customers in the area containing Wheeler, Montgomery, Toombs, Treutlen, and Emanuel Counties is supplied by a single feed originating at the Alamo tap station in Wheeler County.  AGL has undertaken three USF projects thus far to upsize the pipeline exiting the Alamo tap station from 6” to 12” to provide increased supply capability to these counties.  Hydraulic modeling performed in response to this request for service indicates that approximately 28,000 feet of 12” and 18,000 feet of 6” pipe is necessary to provide the 75 MCFH firm load requested by the customer at their location.  The 18,000 feet of 6” pipe is proposed to begin at the intersection of SR 56 and Bream Road (see as-filed MFR-4), which is in the Swainsboro area.

- AGL does not agree that installation of the proposed 6” pipe alone is sufficient to serve this customer.

- No, this incremental load was known prior to filing the 2025 Capacity Supply Plan filing.

- Please see response to STF-17-2c.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-2	MFR 2: The 2025 capital budget used by AGL is incorrect concerning GRAM Other. MFR 2 shows $243,969,318, but the Commission approved $273,959,007. AGL’s numbers in in MFR 2 is $29,989,689 lower than approved. See Table-1 below. All other capital budget dollar amounts are correct. The total dollar amount for FY 2025 was listed as $637,999,762, but the Commission approved  dollar amount is $667,989,452. See Table-2 below. The variance is $29,989,689. AGL will need to refile MFR 2 with the correct GRAM other dollar amounts to achieve a total 2025 capital budget of $667,989,452. The 5% cap dollar amount should be revised to $33,399,473. Does AGL agree to refile MFR-2 with the corrected capital budget and 5% cap information?

Table-1: GRAM Comparison Issue

1st Q 2025 Report				MFR-2

| Table-2: DN 43820: 2025 – 2034 i-CDP Capital Budget |  |  | 2025 |
| --- | --- | --- | --- |
| GRAM - Safety & Compliance (GRAM-S&C) |  |  | $128,140,676.90 |
|  | Distribution Integrity Management Program (DIMP) |  |  |
|  |  | DIMP | $13,000,000.00 |
|  | AC Mitigation Projects |  |  |
|  |  | AC Mitigation | $8,560,000.00 |
|  | Shorted Casing Remediation Program |  |  |
|  |  | Shorted Casings | $7,000,000.00 |
|  | Transmission Integrity Management Program (TIMP) |  |  |
|  |  | TIMP - Dig Program | $74,838,909.84 |
|  |  | TIMP - ILI Retrofits | $0.00 |
|  |  | TIMP - Other (General) | $1,000,000.00 |
|  | Corrosion Control Projects |  |  |
|  |  | Corrosion Projects | $6,581,000.00 |
|  | Rate Base - GRAM-(S&C) Overheads & AFUDC |  |  |
|  |  | RB-GRAM-(S&C) Overheads | $12,427,160.20 |
|  |  | RB-GRAM-(S&C) AFUDC | $4,733,606.86 |
| GRAM - Other than Safety & Compliance (GRAM-Other) |  |  | $273,959,007.39 |
|  | New Business - Core Work |  |  |
|  |  | NB-Core New Business | $109,645,281.13 |
|  |  | NB-New Business PRIM | $8,000,000.00 |
|  | New Business - Large Strategic Efforts |  |  |
|  |  | NB-Other Large/Strat Efforts | $0.00 |
|  |  | NB-USF CNG PSC Funded | $320,664.00 |
|  | New Business - Overheads & AFUDC |  |  |
|  |  | NB-NB Overheads | $13,365,348.00 |
|  |  | NB-NB AFUDC | $1,771,279.21 |
|  | Facilities Projects |  |  |
|  |  | Facilities | $5,871,776.75 |
|  | Fleet Projects |  |  |
|  |  | Fleet | $14,671,580.00 |
|  | IT Projects |  |  |
|  |  | IT-IT Base | $2,130,000.00 |
|  |  | IT-IT Base (Allocations) | $15,839,690.00 |
|  |  | IT-IT MATRIX Ph2 | $5,850,000.00 |
|  |  | IT-IT DTS | $3,510,000.00 |
|  |  | IT-IT ROOT | $4,290,000.00 |
|  |  | IT-IT Marketer Portal | $500,000.00 |
|  | Gas Ops Projects |  |  |
|  |  | Gas Ops-Measurement Ops (SCADA, Ctrls) | $1,988,000.00 |
|  | Strategic Projects |  |  |
|  |  | STRAT-Strategic (Other) | $0.00 |
|  |  | STRAT-Strategic (CNG Stations) | $700,000.00 |
|  | Periodic Testing of Meters |  |  |
|  |  | PT Meter | $9,251,554.16 |
|  | System Renewals (GRAM-Other) |  |  |
|  |  | RENEW-General Renewals | $6,247,209.82 |
|  |  | RENEW-Remote-Controlled Valves | $1,980,000.00 |
|  |  | RENEW-Emergency Districts | $500,000.00 |
|  |  | RENEW-Exposed Mains | $4,000,000.00 |
|  | Operations Support Capital Work |  |  |
|  |  | OPS-Bollard Projects | $1,380,870.79 |
|  |  | OPS-ERT / AMR Projects | $2,426,192.42 |
|  |  | OPS-Blanket Service Renewal Projects | $1,117,366.74 |
|  | Pressure Regulating Facilities, Heaters, & Odorization |  |  |
|  |  | REG STN-Regulator Station Projects | $34,734,203.00 |
|  |  | REG STN-RSRP Program Projects | $2,500,000.00 |
|  | Retirements (Removals) |  |  |
|  |  | REMOV-Removals | $12,149,915.78 |
|  |  | REMOV-Removals (inactive services) | $500,000.00 |
|  | Capitalized Tool Purchases |  |  |
|  |  | Tools (blankets, NB, Field, Con Ops) | $3,120,797.06 |
|  | Rate Base - Overheads & AFUDC |  |  |
|  |  | RB-GRAM-(OTHER) Overheads | $3,899,244.00 |
|  |  | RB-GRAM-(OTHER) AFUDC | $1,698,034.52 |
| RIDER - System Reinforcement Rider (SRR)-Actual Totals |  |  | $149,169,512.50 |
|  | Pressure Improvements (SRR) |  |  |
|  |  | Pressure Improvement (PRIM) - SRR | $7,216,214.40 |
|  | Gas Ops (SRR) |  |  |
|  |  | Gas Ops-Peaking (LNG, Propane, Compression) | $28,375,000.00 |
|  | System Reinforcement - SRR Projects |  |  |
|  |  | SYS RE-Major Pipelines | $79,209,348.02 |
|  |  | SYS RE-Cherokee LNG Expansion Pipelines | $17,032,196.00 |
|  | Rider - (SRR) Overheads & AFUDC |  |  |
|  |  | RIDER-(SRR) Overheads | $6,267,493.54 |
|  |  | RIDER-(SRR) AFUDC | $11,069,260.54 |
| RIDER - DOT |  |  | $50,925,271.53 |
|  | Department of Transportation Driven Projects |  |  |
|  |  | DOT Projects | $44,300,000.00 |
|  |  | DOT Removals | $2,400,000.00 |
|  | Rider - (SRR) Overheads & AFUDC |  |  |
|  |  | RIDER-DOT Overheads | $2,948,280.00 |
|  |  | RIDER-DOT AFUDC | $1,276,991.53 |
| LNG - Cherokee LNG Expansion |  |  | $39,773,771.34 |
|  | Gas Ops (Cherokee LNG Expansion) |  |  |
|  |  | Gas Ops-Cherokee LNG Expansion | $33,609,581.89 |
|  | Rate Base - (Cherokee) Overheads & AFUDC |  |  |
|  |  | (Cherokee) Overheads | $4,549,500.00 |
|  |  | (Cherokee) AFUDC | $1,614,689.45 |
| LNG - Valdosta Satellite LNG |  |  | $11,850,151.27 |
|  | Gas Ops (Valdosta Satellite LNG) |  |  |
|  |  | Gas Ops-Valdosta Satellite LNG | $10,300,000.00 |
|  | Rate Base - (Valdosta) Overheads & AFUDC |  |  |
|  |  | (Valdosta) Overheads | $753,806.45 |
|  |  | (Valdosta) AFUDC | $796,344.82 |
| RIDER - ECON-1 |  |  | $14,171,061.22 |
|  | ECON-1 |  |  |
|  |  | ECON-1 | $13,775,000.00 |
|  | Rate Base - (ECON-1) Overheads & AFUDC |  |  |
|  |  | RIDER-(ECON-1) Overheads | $227,760.00 |
|  |  | RIDER-(ECON-1) AFUDC | $168,301.22 |
| OPS-ERT / AMR Projects - Proposed AMI Technology Program |  |  | $0.00 |
|  | OPS-ERT / AMI Technology Program |  |  |
|  |  | Ops-ERT - AMI Tech | $0.00 |
|  | Rate Base - (AMI) Overheads & AFUDC |  |  |
|  |  | (AMI) Overheads | $0.00 |
|  |  | (AMI) AFUDC | $0.00 |
| DIMP-Pipeline Replacements |  |  | $0.00 |
|  | DIMP - Pipeline Replacements |  |  |
|  |  | DIMP-Replace | $0.00 |
|  | Rate Base - (DIMP-Replace) Overheads & AFUDC |  |  |
|  |  | (DIMP-Replace) Overheads | $0.00 |
|  |  | (DIMP-Replace) AFUDC | $0.00 |
| Renewable Natural Gas Projects |  |  | $0.00 |
|  | Gas Ops (Renewable Natural Gas) |  |  |
|  |  | Gas Ops-RNG | $0.00 |
|  | Rate Base - (RNG) Overheads & AFUDC |  |  |
|  |  | (RNG) Overheads | $0.00 |
|  |  | (RNG) AFUDC | $0.00 |
|  |  | 2025 - 2027 i-CDP Totals (No ECON-1 or DOT) | $602,893,119.40 |
|  |  | DOT | $50,925,272 |
|  |  | DOT Projects | $44,300,000 |
|  |  | DOT Removals | $2,400,000 |
|  |  | RIDER-DOT Overheads & AFUDC | $4,225,272 |
|  |  | ECON-1 | $14,171,061 |
|  |  | ECON-1 | $13,775,000 |
|  |  | RIDER-(ECON-1) Overheads & AFUDC | $396,061 |
|  |  | 2025 - 2027 i-CDP Totals with DOT & ECON-1 | $667,989,452.40 |

RESPONSE

The as-filed capital budget differs from the capital budget approved in GRAM because the as-filed capital budget does not include the IT component as noted in a footnote in the as-filed MFR-2.  Additionally, PSC Rule 515-7-5-.06 limits available funds in the USF for a given fiscal year to $25 million. Consequently, since 5% of AGL’s capital budget exceeds $25 million irrespective of which capital budget number is correct, refiling would not impact funds available under the USF.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-3	MFR-3: Please answer the following:

- Why did the survey responses not include the Emanuel County Project?

- As required in Commission Rule 515-7-5-.07(2)(c)(i)-(10), the public survey must contain certain items. See Table-3 below. The public survey used for MFR-3 did not provide the following:

(i) stakeholders’ response date

(ii) phone numbers

Please provide the missing items.

Table-3: Commission Rule 515-7-5-.07(2)(c)

RESPONSE

AGL requests the information enumerated in Table 3 above in the online survey form.  However, survey respondents sometimes do not provide all of the information requested in the online form.  All survey responses appearing in the as-filed MFR-3 were entered between February 1 and April 30, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-4	MFR 4: Please answer the following:

- Please provide a map showing the Alamo transmission line running from Mt. Vernon to Vidalia showing the size and MAOP of the pipe. Please show and provide details on any distribution main that branches from the transmission line.

- Please provide a map showing the Alamo transmission line running from Vidalia to Lyons showing the size and MAOP of the pipe. Please show and provide details on any distribution main that branches from the transmission line.

RESPONSE

- AGL will respond to this inquiry on or before August 15, 2025.

- AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-5	MFR-5: Please answer the following:

- Why type of gas equipment will the customer use?

- Will the customer operate 8 hours a day,12 hours day, or 24 hours a day?

- What is the volume per Dth per hour, per day, and per year the customer is projected to use?

- Please provide AGL’s estimated five years of annual revenue that this customer will add to AGL revenue requirement and associated ROE? Please list as Year-1, Year-2, Year-3, Year-4, and Year-5.

RESPONSE

- The customer plans to utilize gas-fired dryers.

- It is AGL’s understanding that the plant will operate 5 days per week, 24 hours per day.

- Plant maximum hourly load will be 75 Dth/hr.  It is AGL’s understanding that actual usage is expected to be in the 730 Dth/day, 190,000 Dth/year range.

- AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-6	MFR-6: 3.0 Materials: What procedure did AGL use to calculate the material cost per foot for each pipe size, 4 inch, 6 inch, and 12 inch steel?

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-7	MFR-6: 3.4 Construction: What procedure did AGL use to calculate the labor cost per foot for each pipe size, 4 inch, 6 inch, and 12 inch steel?

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-8	MFR-6: 3.4 Miscellaneous Materials: What does this include?

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-9	MFR-6: 5.1 Risk and Contingency: Please answer the following:

- Please break out all of the components and costs related to this item.

- Please provide the contingency percentage associated with this project and how it was calculated.

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-10	MFR-6: 6.1 Escalation Allowance: Please answer the following:

- What is Escalation Allowance?

- What procedure was used to calculate this estimate?

- When reviewing past USF project’s MFR-6, some have an Escalation Allowances and some do not. Why is this item not always included?

- Why is it necessary to include an Escalation Allowance in an engineering estimate?

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-11	MFR-6: 8.1 Overhead & AFUDC Capitalization Depreciation: Please answer the following:

- Please beak out each component and cost of these items.

- How were these items estimated? Describe in detail.

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource Planning and Economic Development

Southern Company Gas

STF-17-12	MFR-6: 7.1 Direct Internal Labor: Please answer the following:

    - Please beak out each component and cost of these items

    - How were these estimates calculated?

    - Since Overheads include direct internal labor, why is it included again as a separate line item?

RESPONSE

AGL will respond to this inquiry on or before August 15, 2025.

Respondent: 	William “Billy” Horne

Director, Resource, Planning and Economic Development

Southern Company Gas

STF-17-13	MFR-7: Project Technical Analysis: When reviewing AB4, AGL lists a contingency of 50% to 30%, which seems extremely high. Please answer the following:

- Please provide the process AGL used to obtain the contingency percentages.

- Please answer the following:

          - What is the process to build estimates for this project with a 10% contingency?

          - What is the process to build estimates for this project with a 20% contingency?

          - What is the process to build estimates for this project with a 30% contingency?

- In MFR-7, Liberty showed a 75 MCFH for all three sizes of pipe. There were no further discussions about the 75 MCFH in the filing. What is the 75 MCFH related to and should it have been discussed in MFR-1?

- Regarding the Alamo transmission line upgrade between the Alamo tap station and Glenwood, has AGL added any new distribution main and customers since the upgrade was completed, 2019 - 2023? Please list the number of Firm and Interruptible customers added.

RESPONSE

- Contingency refers to a specific allowance within a construction estimate that contemplates project scope changes that may occur during construction.  +50%/-30% is not a contingency percentage.  AGL has discussed the Asset Development Process (“ADP”) utilized by AGL to generate construction estimates with staff multiple times in the past.  To recap a portion of these discussions, ADP consists of five stage gates that develop and refine project estimates.  ADP prescribes that the first stage gate includes a +50%/-30% band to account for unknowns that cannot be foreseen in preparing a stage gate 1 estimate.  As the project unfolds, the estimate is refined through stage gates 2 through 5 as unknowns are identified.  Stage gate 1 estimates are typically presented to the Commission with USF projects.

- The ADP bands referenced in the inquiry could be achieved by executing the ADP process to the stage gate that gives the desired accuracy interval.  Smaller accuracy intervals require additional time and cost to prepare the estimate.

- AGL’s as-filed MFR-7 indicates that 75 MCFH is the customer requested firm load.  Rule 515-7-5-.07(a) covers the requirements of MFR-1 and does not mention customer requested load.  In fact, none of the MFR requirements in Rule 515-7-5-.07 mention customer load requirements.  AGL voluntarily includes load information in MFR-7 because customer load is necessary to perform project technical analysis.

- AGL has added three (3) firm customers to this system since 2019.

Respondent: 	William “Billy” Horne

Director, Resource, Planning and Economic Development

Southern Company Gas