# REBUTTAL TESTIMONY OF

# EARL BERRY

# ON BEHALF OF GEORGIA POWER COMPANY

# GEORGIA PUBLIC SERVICE COMMISSION DOCKET NO. 56765

# I.	INTRODUCTION

Q.	PLEASE STATE YOUR NAME, TITLE, AND BUSINESS ADDRESS.

A.	My name is Earl Berry. I am the Vice President of Engineering for Southern Nuclear Company (“Southern Nuclear”). My business address is 3535 Colonnade Parkway, Birmingham, Alabama 35243.

Q.	MR. BERRY, PLEASE SUMMARIZE YOUR EDUCATIONAL AND PROFESSIONAL EXPERIENCE.

A.	I began my academic studies at the University of Kentucky, earning a Bachelor of Science in Chemical Engineering in 2000. Following this, I pursued a Master of Business Administration at National University. I started my career in the energy industry in 2000 as a Process Engineer and Project Manager at Texaco (later Chevron), where I led and supported multiple energy and emerging technology projects, including gasification and hydrogen. Prior to joining Southern Nuclear, I held engineering leadership positions in advanced energy and technology organizations including Director of Engineering, Engineering Manager, and Process Evaluation Manager for a series of energy startup companies.

In 2009, I joined Southern Nuclear and served in a series of progressively responsible leadership roles including Chemistry Engineer, Rapid Response Engineer, Engineering Components Supervisor, Manager of Site Projects, and Engineering Systems Manager. I advanced to the role of Engineering Director in 2016, and Work Management Director in 2018. I hold an ANSI Senior Reactor Operator certification, which further grounds my leadership experience in licensed nuclear power plant operations. Beginning in June 2019, I served as the Organizational Effectiveness Manager before I was seconded in February 2020 to the Institute of Nuclear Power Operators (“INPO”) to serve as the Organization Effectiveness Leader supporting industry-wide performance improvement. I returned to Southern Nuclear in August of 2021 as the Governance and Oversight General Manager, and in June of 2022, I became the Vice President of Engineering. In this position, I am responsible for enterprise engineering governance, nuclear safety, equipment reliability, regulatory compliance, and executive oversight of engineering performance across the Southern Nuclear Fleet. I engage with the nuclear industry and am the executive sponsor of industry initiatives in accident tolerant fuel and digital modernization.

Q. 	PLEASE DESCRIBE SOUTHERN NUCLEAR OPERATING COMPANY.

A. 	Southern Nuclear is a subsidiary of Southern Company and operates two nuclear electric generating plants on behalf of Georgia Power Company (“Georgia Power”) and its co-owners: the Edwin I. Hatch Nuclear Plant located near Baxley, Georgia; and the Vogtle Electric Generating Plant located near Waynesboro, Georgia. Plant Hatch and Plant Vogtle are co-owned by Georgia Power, Oglethorpe Power Company, the Municipal Electric Authority of Georgia, and the City of Dalton, Georgia through Dalton Utilities. Southern Nuclear has been licensed to operate Plant Hatch and Plant Vogtle since March 1997, when operating responsibility was transferred from Georgia Power to Southern Nuclear. Southern Nuclear also operates the Joseph M. Farley Nuclear Plant, located near Dothan, Alabama, for Alabama Power Company.

Q.	MR. BERRY, HAVE YOU PREVIOUSLY TESTIFIED BEFORE THIS COMMISSION?

A.	No.

Q.	WHAT IS THE PURPOSE OF YOUR REBUTTAL TESTIMONY?

A.	My rebuttal testimony responds to the Direct Testimony of Public Interest Advocacy (“PIA”) Staff Witness Joseph R. Reynolds and provides additional context for the nuclear outages addressed in Mr. Reynolds’ testimony.

Q.	PLEASE SUMMARIZE YOUR TESTIMONY.

A.	My rebuttal testimony responds to PIA Staff Witness Reynolds’ testimony and his recommendations regarding five of the Company’s unplanned nuclear outages by providing additional context and explanation for each event. Witness Reynolds’ investigation did not consider the totality of the facts regarding each event and did not support his assertion that each outage was “clearly imprudent,” as he defines the standard in his own testimony. With this background, my rebuttal testimony attempts to fill in the gaps and clarify the events surrounding the outages and the appropriateness of the Company’s actions and responses in turn.

# II.	NUCLEAR OUTAGES

Q.	PLEASE PROVIDE YOUR GENERAL FEEDBACK IN RESPONSE TO WITNESS REYNOLDS’ TESTIMONY.

A.	Witness Reynolds’ recommendations in this proceeding are based on the information contained in certain reports written by Plant Hatch and Plant Vogtle personnel (Condition Reports, Apparent Cause reports, and Root Cause Analyses). However, in citing these reports, Witness Reynolds does not address the fundamental differences between the purpose of the analysis conducted for such reports and the determination of prudence that occurs in the context of this proceeding.

The reports relied upon were not written with the goal of analyzing whether the decisions in question were reasonable given what was known at the time. Instead, the reports utilize hindsight to identify the potential causes of the incident in question, whether such causes could have been avoided through the application of reasonable management decisions at the time of the event. The goal of identifying possible causes of an event is quite different from evaluating whether the actions or decisions in question were reasonable given the circumstances that existed at that time. Often, these reports are based on information that was not available at the time the underlying decisions were made or they omit key background information or other general issues that were considered by the decisionmakers.

Further, Witness Reynolds only presents selected portions of the material included in the reports, which provide insufficient context for the Commission’s review. The terminology utilized in such reports often has meanings that are specific to the goals and ends of such reports. For example, “inadequate” connotes that the relevant actions or decisions did not result in the desired outcome but does not mean that the actions or decisions were unreasonable or reflective of a lack of diligence and care by Company employees. Thus, to use these reports as Witness Reynolds has, without proper context or independent analyses, risks misinterpreting or misconstruing such reports and the actions taken in response to certain events. In particular, the Root Cause and Apparent Cause reports typically do not delve into the underlying basis or rationale for a decision, such as why an engineer, technician, or operator took a particular action, but rather, summarily conclude that the decision did not lead to the desired result.

Q.	DO YOU STAND BEHIND THE ACCURACY AND COMPLETENESS OF THE REPORTS?

# A.	Yes. I am extremely proud of the strength of our evaluative process as reflected in these reports. I, along with all of Southern Nuclear’s leadership, encourage thorough and exhaustive analysis of these outages in order to identify every possible corrective action that could have been taken to better inform practice and process improvements to prevent such events from reoccurring. We apply a very high standard to our causal analysis findings and corrective actions consistent with nuclear industry measures of excellence. It is important to note, however, that the purpose of post-event causal analysis is to find opportunities for improvement using information that is available only after the event occurs. Accordingly, these analyses intentionally apply a high standard and benefit from hindsight and are not necessarily designed to assess whether decisions made prior to the event are reasonable based on the information available at that time. We acknowledge that not all processes are perfect and there are always opportunities for improvement and the causal analyses bear that fact. However, the Company’s efforts to constantly improve our processes and performance should not be construed as evidence of imprudence.

Q.	ARE THE CONCLUSIONS DRAWN IN THE REPORTS A SUBSTITUTE FOR MANAGEMENT’S DECISION-MAKING PROCESS?

# A.	No. Southern Nuclear management closely reviews the reports and engages in a deliberative process to implement any necessary corrective actions. Southern Nuclear management must also balance numerous other considerations and challenges in determining the appropriate course of action (e.g., timing, technology interplay, cost, etc.).

Q.	DOES SOUTHERN NUCLEAR EXPECT AND ACCEPT THAT FORCED OUTAGES WILL OCCUR?

# A.	No, absolutely not. Southern Nuclear expects complete operational excellence. We strive to have zero mistakes and no unplanned or forced outages, and our employees are consistently reminded of this objective, along with the overriding goal of safety that controls every decision made at the plants. This goal is exactly why Southern Nuclear conducts Root Cause and Apparent Cause analyses without regard for cost or what was actually or reasonably known at the time. Southern Nuclear intends to utilize every resource and every avenue for improvement that is available. My testimony is not intended to trivialize the outages that occurred or minimize the importance of the additional fuel costs incurred. Rather, the purpose of this testimony is to place each event in its proper context and focus attention on the facts and circumstances as they existed at the time of each incident, including key decisions leading up to these events.

Q.	PLEASE ELABORATE ON THE SIGNIFICANCE OF THE FACT THAT PIA STAFF ONLY IDENTIFIED FIVE OUTAGES FOR RECOMMENDED DISALLOWANCE.

A.	While it is the Company’s position that none of these outages were the result of imprudent actions or decisions, the fact that Witness Reynolds only recommended disallowance of replacement fuel cost for five outages is a testament to the high level at which the Company operates these plants. Over the three-year period covered by this proceeding, Plants Hatch and Vogtle have contributed 64,802,106 megawatt hours (“MWh”) of low-cost, emission free generation to Georgia Power’s customers. Over that same time, Witness Reynolds only identified five outages for potential disallowance, representing 831,229 MWh of lost generation (or just 1.3% of the total generation during the historic period). I believe that the excellent operation of our plants over that time should be considered by the Commission as it reviews these particular outages.

Q.	DOES THE EFFECTIVENESS OF SOUTHERN NUCLEAR’S FLEET FIGURE INTO THE CONTEXT OF THE INCIDENTS DISCUSSED IN MR. REYNOLDS’ TESTIMONY?

# A.	Yes. Southern Nuclear’s excellent and cost-effective performance provides the context necessary to truly understand why the decisions that Southern Nuclear made—based upon known facts and competing priorities at the time, as the prudence standard requires—were reasonable. In particular, Southern Nuclear has a demonstrated history of success in reducing the impact of unplanned outages. Although there are no criteria that measure “prudence,” there are metrics for the reliability of nuclear plants. One of these metrics is called the Capacity Factor, a measure of how often a power plant runs over a specific period of time. The Capacity Factor is expressed as a percentage and calculated by dividing the actual unit electricity output by the maximum possible output. This ratio indicates how fully a unit’s capacity is used. The Capacity Factor of Southern Nuclear’s Georgia fleet (not including Vogtle Units 3 and 4) over the previous three years is 93.63%. This is in line with the average of 93.2% for nuclear power generation in the United States. Vogtle Units 3 and 4 do not have three full years of service at this point and, as previously discussed with the Commission, Unit 4 was operated at a lower power level to extend fuel life.

Q.	WHY ARE THESE OBSERVATIONS NECESSARY TO ASSESS THE REASONABLENESS OF SOUTHERN NUCLEAR’S ACTIONS IN THESE INCIDENTS?

# A.	The success of Southern Nuclear’s fleet on metrics of cost, production, efficiency, and safety could not be achieved without a culture of safety, reliability, and sensible decision making that benefits Georgia Power’s customers. Each of these metrics (cost, production, efficiency, safety, etc.) is a priority that Southern Nuclear has an obligation to weigh for the benefit of customers. The Root Cause and Apparent Cause reports, which Witness Reynolds relies upon, are not written within this framework. Rather, these reports go above and beyond to find any possible causes of the incident analyzed, specifically with intent to identify means of improvement going forward.

III.	PLANT HATCH

A.	PLANT HATCH UNIT 2 EVENT 26 (09/13/2025)

Q.	PLEASE DESCRIBE THE CIRCUMSTANCES OF THE OUTAGE THAT OCCURRED AT PLANT HATCH UNIT 2 ON SEPTEMBER 13, 2025.

A.	On September 13, 2025, Hatch Unit 2 Operators were performing required turbine valve testing. On the fourth and final test, the unit experienced a trip of both REDACTED REDACTED. A manual SCRAM was inserted per site procedure and industry norms.

Q.	WERE SOUTHERN NUCLEAR’S ACTIONS LEADING UP TO AND DURING THE SEPTEMBER 13, 2025 HATCH UNIT 2 EVENT REASONABLE AND PRUDENT?

A. 	Yes, Southern Nuclear’s actions before and during the September 13, 2025 Hatch Unit 2 event were reasonable and prudent when evaluated based on the information available at the time and consistent with industry standards and plant procedures.

Prior to the event, the unit was operating within its approved configuration, and turbine valve testing was being performed in accordance with established procedures. There was no indication that conditions existed that would have caused this event. Three of four turbine valves had been successfully tested. Following the event, Southern Nuclear conducted thorough causal analysis to understand all the factors contributing to the event and identify appropriate corrective actions. These reviews were undertaken not because the pre-event decisions were imprudent, but because Southern Nuclear holds itself to a high standard of continuous improvement. Notably, the Root Cause Analysis did not find that the Company had inadequate procedures in place at the time of the event. Further, the occurrence of the event does not show that management or operational decisions were unreasonable given the facts and circumstances known at the time.

Q.	WHY SHOULD THE CONCLUSIONS OF POST-EVENT CAUSAL ANALYSIS NOT BE USED TO JUDGE THE PRUDENCE OF PRE-EVENT DECISION MAKING?

A.	As stated above, the purpose of post-event causal analysis is to find opportunities for improvement using information that becomes available only after the event occurs. These analyses purposefully apply a high standard and benefit from hindsight. As such, they are not designed to evaluate whether decisions made prior to the event are reasonable based on the information available at the time the event occurred. In this case, Southern Nuclear’s procedures, policies, and training reflect sound operational judgement and a conservative bias toward safety as three of four valves had already been successfully tested. The fact that improvement opportunities were found does not mean that the original procedures or policies were imprudent.

Q.	DOES WITNESS REYNOLDS’ CONCLUSION THAT THIS OUTAGE WAS IMPRUDENT FIT WITHIN HIS OWN DEFINITION OF IMPRUDENCE?

A.	No. Witness Reynolds describes a plethora of factors to be evaluated in determining if an outage is prudently incurred or the result of clear imprudence. He testifies that if such analysis “indicate[s] that this was a one-time mistake by the plant operator, I would likely conclude that the operator was imprudent in that he did not take adequate care . . . . When I discover a pattern of similar events, and actions to prevent this type of event were inadequate or not timely, I would likely conclude this outage to be clearly imprudent.” Here, Witness Reynolds’ has failed to identify a pattern or similar events that would support a finding under his analysis of clear imprudence. He cites no similar events, and in fact, omits the fact that the Company had already performed three tests. In addition, on page 18 of his testimony, Witness Reynolds acknowledges that the Company’s steps and procedures were adequate.

# B.	PLANT HATCH UNIT 2 EVENT 23, 11/01/2023

Q.	PLEASE DESCRIBE THE CIRCUMSTANCES OF THE OUTAGE THAT OCCURRED AT PLANT HATCH UNIT 2 ON NOVEMBER 1, 2023.

A.	On November 13, 2023, Hatch Unit 2 had a REDACTED REDACTED REDACTED for the REDACTED REDACTED, which caused a leak. Operators secured one of the two REDACTED REDACTED to reduce the leakage. The second REDACTED REDACTED automatically tripped due to water from the leak. Operators inserted a manual SCRAM as Reactor water levels dropped. The impacted REDACTED REDACTED is not nuclear safety-related; therefore, the Maintenance team was deployed to fix the broken bracket.

Q.	WERE SOUTHERN NUCLEAR’S ACTIONS LEADING UP TO AND DURING THE NOVEMBER 13, 2023 HATCH UNIT 2 EVENT REASONABLE AND PRUDENT?

A.	Yes. Southern Nuclear’s actions associated with the November 13, 2023, event were reasonable and prudent when evaluated based on the conditions and information known at the time. The event was started by a pipe failure. Once the leak occurred, Operators responded conservatively and in accordance with approved procedures. When water intrusion caused the second REDACTED REDACTED to trip and REDACTED water level to drop, Operators inserted a manual SCRAM per approved procedures and industry norms.

Q.	DOES THE FACT THAT A REDACTED FAILURE LED TO THE OUTAGE MEAN THAT SOUTHERN NUCLEAR’S PRIOR DECISION WAS IMPRUDENT?

A.	No. Equipment failures, particularly REDACTED REDACTED, can occur without prior warning notwithstanding the application of sound engineering, maintenance, and/or operational practices. Southern Nuclear has robust programs in place for system health monitoring, corrective actions, and continuous improvement, but the occurrence of equipment failures does not show that pre-event decisions were unreasonable. For this event, it is reasonable for Maintenance to fix a broken part and return it to the previous state.

Q.	DOES THE FACT THAT THERE WAS EARLIER REDACTED FAILURE MEAN THAT SOUTHERN NUCLEAR’S ACTIONS WERE TO RESTORE THE BROKEN PART WERE IMPRUDENT?

A.	No. In hindsight, our causal analysis noted a missed opportunity to find earlier failures and look deeper into the core issue. Although the causal analysis identified failures in 2007, notably there were no other failures until 2023. So, it is reasonable for Maintenance personnel to assume the needed fix was to reinstall the bracket given reasonable operation for a period of 16 years. Additionally, as noted in our causal analysis, both Maintenance and Operations personnel assumed simple vibration was the core issue. With that in mind, the Maintenance and Operations personnel assumed that reinstallation of the bracket was the right action.

# IV.	PLANT VOGTLE

# A.	PLANT VOGTLE UNIT 3 EVENT 86 (09/17/2024)

Q.	PLEASE DESCRIBE THE CIRCUMSTANCES OF THE OUTAGE THAT OCCURRED AT PLANT VOGTLE UNIT 3 ON SEPTEMBER 17, 2024.

A.	On September 17, 2024, Vogtle Unit 3 experienced a REDACTED failure leading to a REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED opening completely instead of staying closed. This led to an automatic SCRAM and Safeguards actuation.

Q.	WERE SOUTHERN NUCLEAR’S ACTIONS LEADING UP TO AND DURING THE SEPTEMBER 17, 2024 VOGTLE UNIT 3 EVENT REASONABLE AND PRUDENT?

A.	Yes. Southern Nuclear’s actions related to the September 17, 2024 Vogtle Unit 3 event were reasonable and prudent based on the information available at the time and were consistent with plant design, procedures, and industry standards. This event was caused by an unexpected REDACTED failure.

At the time of the event, Vogtle Unit 3 was operating within its approved configuration, and there were no indications that this particular REDACTED failure or valve response was imminent or reasonably foreseeable. The REDACTED were obtained as safety-related components consistent with industry standards. The plant’s protection systems functioned as designed and intended and operators responded appropriately.

The vulnerability of this single REDACTED failure is part of the original plant design. The AP-1000 design is certified by the Nuclear Regulatory Commission (“NRC”) in accordance with 10 Code of Federal Regulations Part 52. Per the terms of 10 C.F.R. Part 52, significant changes to the core design are not permitted without reapproval by the NRC. As noted in the causal analysis, following completion of construction, Southern Nuclear initiated a design change with the original equipment manufacturer (“OEM”).

As with other post-event reviews, these analyses benefited from hindsight and were conducted to strengthen long-term reliability and performance. The improvement opportunities identified after the fact do not indicate pre-event decisions or maintenance practices were unreasonable given the original plant design as approved by the NRC.

Q. 	COULD THIS OUTAGE HAVE BEEN PREVENTED BASED ON THE CRITICALITY RANKING OF THE REDACTED AS SUGGESTED BY PIA STAFF WITNESS REYNOLDS?

A.	No. As stated in the Southern Nuclear causal product, the REDACTED were noted as a single point vulnerability (“SPV”) and the criticality of the part would not have prevented the REDACTED failure. Southern Nuclear utilizes the Electric Power Research Institute (“EPRI”) recommendations for REDACTED maintenance. These REDACTED were categorized as “Run to Maintenance” and the SPV plan lists replacement of the REDACTED with valve maintenance at no later than 10 years. The causal analysis noted this was not an issue or contributor to the failure of the REDACTED since these REDACTED were less than 10 years old at the time of failure. In fact, these REDACTED were replaced after construction was completed and prior to commercial operation to maximize the potential for satisfactory performance.

The Company’s response to this REDACTED failure was not clearly imprudent, nor was it imprudent. The REDACTED were installed as designed and approved by the NRC. Contrary to the statements of Witness Reynolds, additional or more regular maintenance on this type of component does more harm than good because it introduces infinitely more opportunities for failure. REDACTED fail when they are installed incorrectly. To check a REDACTED, the maintenance engineer must uninstall and reinsert it, which not only introduces oil from a human hand, it increases the likelihood that the REDACTED is reinstalled incorrectly. REDACTED like these are the type of component best left alone and not touched until a major system outage is scheduled.

# B.	PLANT VOGTLE UNIT 3 EVENT 66 (07/08/2024)

Q.	PLEASE DESCRIBE THE CIRCUMSTANCES OF THE OUTAGE THAT OCCURRED AT PLANT VOGTLE UNIT 3 ON JULY 8, 2024.

A.	On July 8, 2024, Vogtle Unit 3 REDACTED REDACTED REDACTED failed to the open position due to foreign material in a positioner internal pressure regulator. This failure led to a loss of forward flow, causing the water levels in both Steam Generators to drop. Operators inserted a manual SCRAM due to low water levels in the Steam Generators.

Q.	WERE SOUTHERN NUCLEAR’S ACTIONS LEADING UP TO AND DURING THE JULY 8, 2024 VOGTLE UNIT 3 EVENT REASONABLE AND PRUDENT?

A.	Yes. Southern Nuclear’s actions related to the July 8, 2024 Vogtle Unit 3 event were reasonable and prudent based on the information available at the time and consistent with plant design, procedures, and industry standards.

At the time of the event, Vogtle Unit 3 was operating within its approved configuration, and there were no indications that the REDACTED REDACTED within the REDACTED was present or that the REDACTED would fail in this manner. The positioner in question is located inside another component and not visible upon initial inspection without taking apart the surrounding component. Further, the REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED REDACTED. The positioner was installed during plant construction and follow up inspections of similar positioners found no similar issues.

Even within Mr. Reynolds’ own definitions of imprudence and clear imprudence, the failure to REDACTED REDACTED REDACTED component located inside of another component does not come close to imprudent decision making or conduct of the Company. Further, the REDACTED was introduced by the manufacturer, not the Company. No Company conduct, omission, or oversight contributed to this outage.

C.	PLANT VOGTLE UNIT 4 EVENT 10 (06/05/2024)

Q.	PLEASE DESCRIBE THE CIRCUMSTANCES OF THE OUTAGE THAT OCCURRED AT PLANT VOGTLE UNIT 4 ON JUNE 5, 2024.

A.	On June 5, 2024, Vogtle Unit 4 Operators inserted a manual SCRAM after they responded in an unexpected manner following the trip of the REDACTED REDACTED. A faulty temperature probe gave a high REDACTED REDACTED REDACTED for the REDACTED REDACTED. This resulted in an automatic Turbine Runback and REDACTED REDACTED REDACTED. REDACTED buildup, due to the REDACTED, lowered the REDACTED REDACTED REDACTED. However, the REDACTED prevented the REDACTED from adjusting to respond to the lowering temperature.

Q.	WERE SOUTHERN NUCLEAR’S ACTIONS LEADING UP TO AND DURING THE JUNE 5, 2024 VOGTLE UNIT 4 EVENT REASONABLE AND PRUDENT?

A.	Yes. Southern Nuclear’s actions related to the June 5, 2024 Vogtle Unit 4 event were reasonable and prudent based on the information available at the time and consistent with plant design, approved procedures, and operator training.

The event started with a faulty temperature probe that provided an erroneous high REDACTED REDACTED REDACTED REDACTED. This REDACTED REDACTED was installed during construction of the plant. There were no indications that the REDACTED was faulty prior to the failure.

Following the outage, Southern Nuclear conducted the causal analyses to fully understand the failure. As with other analyses, the causal product was the result of hindsight and was prepared with the intent of furthering continuous improvement. Southern Nuclear identified that this REDACTED was not installed correctly, but there were no indications of similar issues with other REDACTED. Also, it was found that none of the construction documents indicated any issues during installation.

Q.	IS THIS COMPONENT SUBJECT TO ANY WARRANTY UPON WHICH THE COMPANY COULD DRAW TO BE COMPENSATED FOR THIS FAILURE AS SUGGESTED BY PIA STAFF WITNESS REYNOLDS?

A.	No.  Witness Reynolds’ suggestion that this is a warranty item underscores his unfamiliarity with typical nuclear industry practice and the Vogtle Units 3 and 4 Project. In addition to the significant passage of time and the Westinghouse bankruptcy resulting in warranties no longer being available, warranties that were previously available would not cover the costs at issue here.  Vendors will not agree to warranty terms where they agree to bear indirect damages due to unit outages and downpowers, or in the unlikely event they would it would render their components cost-prohibitive.  A warranty of the kind Witness Reynolds discusses is not a standard or expected practice in the nuclear industry.

# V.	CONCLUSION

Q.	WERE THE COMPANY’S ACTIONS AND DECISION MAKING REGARDING THESE OUTAGES CLEARLY IMPRUDENT?

A.	No. The Company’s actions and decisions related to the outages addressed above were reasonable and prudent and did not evidence any unaddressed reoccurrence trend or repeat deficiency. Witness Reynolds’ testimony does not support a finding of clear imprudence for any of the five outages addressed. His attempt to identify a common thread among these outages is an overgeneralization that does not appropriately consider the full context of the circumstances impacting each outage.

Q.	DOES THIS CONCLUDE YOUR REBUTTAL TESTIMONY?

A.	Yes.

See Table 6.07.B Capacity Factors for Utility Scale Generators Primarily Using Non-Fossil Fuels, U.S. Energy Information Administration, available at https://www.eia.gov/electricity/monthly/epm_table_grapher.php?t=epmt_6_07_b